## Wire
Wire data from PJM's published overhead rating sheet and from SouthWire.
https://www.pjm.com/-/media/planning/design-engineering/maac-standards/oht-cond-rating-spreadsheet.ashx
Accessed 10/26/2023
Additional data has been added as needed from other sources. For additional publically available Southwire conductor specs, please use their website at
https://www.southwire.com/
Name | CodeWord | Size | Cond Strand | Core Strand | Cond Wire Dia | Core Wire Dia | Core OD | Metal OD | Strand Lay | TW Type | TW Layers | Low Temp | Low Resistance | Hi Temp | Hi Resistance | Al Weight | St Weight | Values From | WireKey
AAAC | Akron | 30.58 | 7 |  | 0.0661 |  |  | 0.198 |  |  |  | 25 | 3.5394 | 75 | 4.143 | 28.5 |  | Southwire | AAAC : 30.58 : Akron : 7
AAAC | Alton | 48.69 | 7 |  | 0.0834 |  |  | 0.25 |  |  |  | 25 | 2.2235 | 75 | 2.6026 | 45.4 |  | Southwire | AAAC : 48.69 : Alton : 7
AAAC | Ames | 77.47 | 7 |  | 0.1052 |  |  | 0.316 |  |  |  | 25 | 1.3973 | 75 | 1.6355 | 72.2 |  | Southwire | AAAC : 77.47 : Ames : 7
AAAC | Azusa | 123.3 | 7 |  | 0.1327 |  |  | 0.398 |  |  |  | 25 | 0.8782 | 75 | 1.0278 | 114.9 |  | Southwire | AAAC : 123.3 : Azusa : 7
AAAC | Anaheim | 155.4 | 7 |  | 0.149 |  |  | 0.447 |  |  |  | 25 | 0.6969 | 75 | 0.8156 | 144.9 |  | Southwire | AAAC : 155.4 : Anaheim : 7
AAAC | Amherst | 195.7 | 7 |  | 0.1672 |  |  | 0.502 |  |  |  | 25 | 0.5536 | 75 | 0.6478 | 182.5 |  | Southwire | AAAC : 195.7 : Amherst : 7
AAAC | Alliance | 246.9 | 7 |  | 0.1878 |  |  | 0.563 |  |  |  | 25 | 0.4391 | 75 | 0.5137 | 230.2 |  | Southwire | AAAC : 246.9 : Alliance : 7
AAAC | Amarillo | 246.9 | 19 |  | 0.114 |  |  | 0.57 |  |  |  | 25 | 0.4391 | 75 | 0.5137 | 230.3 |  | Southwire | AAAC : 246.9 : Amarillo : 19
AAAC | Butte | 312.8 | 19 |  | 0.1283 |  |  | 0.642 |  |  |  | 25 | 0.3469 | 75 | 0.4058 | 291.6 |  | Southwire | AAAC : 312.8 : Butte : 19
AAAC | Canton | 394.5 | 19 |  | 0.1441 |  |  | 0.721 |  |  |  | 25 | 0.2755 | 75 | 0.3221 | 367.9 |  | Southwire | AAAC : 394.5 : Canton : 19
AAAC | Cairo | 465.4 | 19 |  | 0.1565 |  |  | 0.783 |  |  |  | 25 | 0.2339 | 75 | 0.2733 | 433.9 |  | Southwire | AAAC : 465.4 : Cairo : 19
AAAC | Darien | 559.5 | 19 |  | 0.1716 |  |  | 0.858 |  |  |  | 25 | 0.195 | 75 | 0.2278 | 521.7 |  | Southwire | AAAC : 559.5 : Darien : 19
AAAC | Elgin | 652.4 | 19 |  | 0.1853 |  |  | 0.927 |  |  |  | 25 | 0.1677 | 75 | 0.1958 | 608.3 |  | Southwire | AAAC : 652.4 : Elgin : 19
AAAC | Flint | 740.8 | 37 |  | 0.1415 |  |  | 0.991 |  |  |  | 25 | 0.1482 | 75 | 0.1728 | 690.8 |  | Southwire | AAAC : 740.8 : Flint : 37
AAAC | Greeley | 927.2 | 37 |  | 0.1583 |  |  | 1.108 |  |  |  | 25 | 0.1193 | 75 | 0.1389 | 864.6 |  | Southwire | AAAC : 927.2 : Greeley : 37
AAC | Peachbell | 6 | 7 |  | 0.0612 |  |  | 0.184 |  |  |  | 25 | 3.5471 | 75 | 4.2493 | 24.6 |  | Southwire | AAC : 6 : Peachbell : 7
AAC | Rose | 4 | 7 |  | 0.0772 |  |  | 0.232 |  |  |  | 25 | 2.2308 | 75 | 2.6725 | 39.1 |  | Southwire | AAC : 4 : Rose : 7
AAC | Iris | 2 | 7 |  | 0.0974 |  |  | 0.292 |  |  |  | 25 | 1.4031 | 75 | 1.6808 | 62.2 |  | Southwire | AAC : 2 : Iris : 7
AAC | Pansy | 1 | 7 |  | 0.1093 |  |  | 0.328 |  |  |  | 25 | 1.1128 | 75 | 1.333 | 78.4 |  | Southwire | AAC : 1 : Pansy : 7
AAC | Poppy | 1/0 | 7 |  | 0.1228 |  |  | 0.368 |  |  |  | 25 | 0.8829 | 75 | 1.0576 | 98.9 |  | Southwire | AAC : 1/0 : Poppy : 7
AAC | Aster | 2/0 | 7 |  | 0.1379 |  |  | 0.414 |  |  |  | 25 | 0.7 | 75 | 0.8384 | 124.8 |  | Southwire | AAC : 2/0 : Aster : 7
AAC | Phlox | 3/0 | 7 |  | 0.1548 |  |  | 0.464 |  |  |  | 25 | 0.5543 | 75 | 0.6652 | 157.2 |  | Southwire | AAC : 3/0 : Phlox : 7
AAC | Oxlip | 4/0 | 7 |  | 0.1739 |  |  | 0.522 |  |  |  | 25 | 0.4407 | 75 | 0.5277 | 198.4 |  | Southwire | AAC : 4/0 : Oxlip : 7
AAC | Sneezewort | 250 | 7 |  | 0.189 |  |  | 0.567 |  |  |  | 25 | 0.3733 | 75 | 0.4469 | 234.4 |  | Southwire | AAC : 250 : Sneezewort : 7
AAC | Valerian | 250 | 19 |  | 0.1147 |  |  | 0.574 |  |  |  | 25 | 0.3733 | 75 | 0.4469 | 234.3 |  | Southwire | AAC : 250 : Valerian : 19
AAC | Daisy | 266.8 | 7 |  | 0.1953 |  |  | 0.586 |  |  |  | 25 | 0.3499 | 75 | 0.4188 | 250.2 |  | Southwire | AAC : 266.8 : Daisy : 7
AAC | Laurel | 266.8 | 19 |  | 0.1185 |  |  | 0.593 |  |  |  | 25 | 0.3499 | 75 | 0.4188 | 250.1 |  | Southwire | AAC : 266.8 : Laurel : 19
AAC | Peony | 300 | 19 |  | 0.1257 |  |  | 0.629 |  |  |  | 25 | 0.3113 | 75 | 0.3726 | 281.4 |  | Southwire | AAC : 300 : Peony : 19
AAC | Tulip | 336.4 | 19 |  | 0.1331 |  |  | 0.666 |  |  |  | 25 | 0.2779 | 75 | 0.3325 | 315.5 |  | Southwire | AAC : 336.4 : Tulip : 19
AAC | Daffodil | 350 | 19 |  | 0.1357 |  |  | 0.679 |  |  |  | 25 | 0.2672 | 75 | 0.3197 | 327.9 |  | Southwire | AAC : 350 : Daffodil : 19
AAC | Canna | 397.5 | 19 |  | 0.1447 |  |  | 0.724 |  |  |  | 25 | 0.2355 | 75 | 0.2817 | 372.9 |  | Southwire | AAC : 397.5 : Canna : 19
AAC | Goldentuft | 450 | 19 |  | 0.1539 |  |  | 0.769 |  |  |  | 25 | 0.2084 | 75 | 0.2491 | 421.8 |  | Southwire | AAC : 450 : Goldentuft : 19
AAC | Syringa | 477 | 37 |  | 0.1135 |  |  | 0.795 |  |  |  | 25 | 0.1968 | 75 | 0.2352 | 446.8 |  | Southwire | AAC : 477 : Syringa : 37
AAC | Cosmos | 477 | 19 |  | 0.1584 |  |  | 0.793 |  |  |  | 25 | 0.1968 | 75 | 0.2352 | 446.8 |  | Southwire | AAC : 477 : Cosmos : 19
AAC | Hyacinth | 500 | 37 |  | 0.1162 |  |  | 0.813 |  |  |  | 25 | 0.1879 | 75 | 0.2245 | 468.3 |  | Southwire | AAC : 500 : Hyacinth : 37
AAC | Zinnia | 500 | 19 |  | 0.1622 |  |  | 0.811 |  |  |  | 25 | 0.1879 | 75 | 0.2245 | 468.5 |  | Southwire | AAC : 500 : Zinnia : 19
AAC | Misteltoe | 556.5 | 37 |  | 0.1226 |  |  | 0.858 |  |  |  | 25 | 0.1691 | 75 | 0.202 | 521.3 |  | Southwire | AAC : 556.5 : Misteltoe : 37
AAC | Dahlia | 556.5 | 19 |  | 0.1711 |  |  | 0.856 |  |  |  | 25 | 0.1691 | 75 | 0.202 | 521.4 |  | Southwire | AAC : 556.5 : Dahlia : 19
AAC | Meadowsweet | 600 | 37 |  | 0.1273 |  |  | 0.891 |  |  |  | 25 | 0.1571 | 75 | 0.1875 | 562 |  | Southwire | AAC : 600 : Meadowsweet : 37
AAC | Orchid | 636 | 37 |  | 0.1311 |  |  | 0.918 |  |  |  | 25 | 0.1485 | 75 | 0.1771 | 596.1 |  | Southwire | AAC : 636 : Orchid : 37
AAC | Flag | 700 | 61 |  | 0.1071 |  |  | 0.964 |  |  |  | 25 | 0.1353 | 75 | 0.1613 | 655.8 |  | Southwire | AAC : 700 : Flag : 61
AAC | Verbena | 700 | 37 |  | 0.1375 |  |  | 0.963 |  |  |  | 25 | 0.1353 | 75 | 0.1613 | 655.7 |  | Southwire | AAC : 700 : Verbena : 37
AAC | Nasturtium | 715.5 | 61 |  | 0.1083 |  |  | 0.975 |  |  |  | 25 | 0.1325 | 75 | 0.1578 | 670.6 |  | Southwire | AAC : 715.5 : Nasturtium : 61
AAC | Violet | 715.5 | 37 |  | 0.1391 |  |  | 0.974 |  |  |  | 25 | 0.1325 | 75 | 0.1578 | 671 |  | Southwire | AAC : 715.5 : Violet : 37
AAC | Cattail | 750 | 61 |  | 0.1109 |  |  | 0.998 |  |  |  | 25 | 0.1266 | 75 | 0.1508 | 703.2 |  | Southwire | AAC : 750 : Cattail : 61
AAC | Petunia | 750 | 37 |  | 0.1424 |  |  | 0.997 |  |  |  | 25 | 0.1266 | 75 | 0.1508 | 703.2 |  | Southwire | AAC : 750 : Petunia : 37
AAC | Lilac | 795 | 61 |  | 0.1142 |  |  | 1.028 |  |  |  | 25 | 0.1197 | 75 | 0.1425 | 745.7 |  | Southwire | AAC : 795 : Lilac : 61
AAC | Arbutus | 795 | 37 |  | 0.1466 |  |  | 1.026 |  |  |  | 25 | 0.1197 | 75 | 0.1425 | 745.3 |  | Southwire | AAC : 795 : Arbutus : 37
AAC | Crocus | 874.5 | 61 |  | 0.1198 |  |  | 1.078 |  |  |  | 25 | 0.109 | 75 | 0.13 | 820.6 |  | Southwire | AAC : 874.5 : Crocus : 61
AAC | Anemone | 874.5 | 37 |  | 0.1538 |  |  | 1.077 |  |  |  | 25 | 0.109 | 75 | 0.1298 | 820.3 |  | Southwire | AAC : 874.5 : Anemone : 37
AAC | Snapdragon | 900 | 61 |  | 0.1215 |  |  | 1.094 |  |  |  | 25 | 0.1064 | 75 | 0.1264 | 844 |  | Southwire | AAC : 900 : Snapdragon : 61
AAC | Cockscomb | 900 | 37 |  | 0.156 |  |  | 1.092 |  |  |  | 25 | 0.1064 | 75 | 0.1264 | 844 |  | Southwire | AAC : 900 : Cockscomb : 37
AAC | Goldenrod | 954 | 61 |  | 0.1251 |  |  | 1.126 |  |  |  | 25 | 0.1007 | 75 | 0.1195 | 894.8 |  | Southwire | AAC : 954 : Goldenrod : 61
AAC | Magnolia | 954 | 37 |  | 0.1606 |  |  | 1.124 |  |  |  | 25 | 0.1007 | 75 | 0.1195 | 894.5 |  | Southwire | AAC : 954 : Magnolia : 37
AAC | Cameilla | 1000 | 61 |  | 0.128 |  |  | 1.152 |  |  |  | 25 | 0.0963 | 75 | 0.1142 | 936.8 |  | Southwire | AAC : 1000 : Cameilla : 61
AAC | Hawkweed | 1000 | 37 |  | 0.1644 |  |  | 1.15 |  |  |  | 25 | 0.0963 | 75 | 0.1142 | 937.3 |  | Southwire | AAC : 1000 : Hawkweed : 37
AAC | Larkspur | 1033.5 | 61 |  | 0.1302 |  |  | 1.172 |  |  |  | 25 | 0.0934 | 75 | 0.1107 | 969.2 |  | Southwire | AAC : 1033.5 : Larkspur : 61
AAC | Bluebell | 1033.5 | 37 |  | 0.1671 |  |  | 1.17 |  |  |  | 25 | 0.0934 | 75 | 0.1107 | 968.3 |  | Southwire | AAC : 1033.5 : Bluebell : 37
AAC | Marigold | 1113 | 61 |  | 0.1351 |  |  | 1.216 |  |  |  | 25 | 0.0872 | 75 | 0.1032 | 1044 |  | Southwire | AAC : 1113 : Marigold : 61
AAC | Hawthorn | 1192.5 | 61 |  | 0.1398 |  |  | 1.258 |  |  |  | 25 | 0.0819 | 75 | 0.0967 | 1117 |  | Southwire | AAC : 1192.5 : Hawthorn : 61
AAC | Narcissus | 1272 | 61 |  | 0.1444 |  |  | 1.3 |  |  |  | 25 | 0.0772 | 75 | 0.0912 | 1192 |  | Southwire | AAC : 1272 : Narcissus : 61
AAC | Columbine | 1351.5 | 61 |  | 0.1488 |  |  | 1.34 |  |  |  | 25 | 0.0731 | 75 | 0.0861 | 1266 |  | Southwire | AAC : 1351.5 : Columbine : 61
AAC | Carnation | 1431 | 61 |  | 0.1532 |  |  | 1.379 |  |  |  | 25 | 0.0695 | 75 | 0.0817 | 1342 |  | Southwire | AAC : 1431 : Carnation : 61
AAC | Galdious | 1510.5 | 61 |  | 0.1574 |  |  | 1.417 |  |  |  | 25 | 0.0663 | 75 | 0.0778 | 1417 |  | Southwire | AAC : 1510.5 : Galdious : 61
AAC | Coreopsis | 1590 | 61 |  | 0.1614 |  |  | 1.454 |  |  |  | 25 | 0.0635 | 75 | 0.0743 | 1489 |  | Southwire | AAC : 1590 : Coreopsis : 61
AAC | Jessamine | 1750 | 61 |  | 0.1694 |  |  | 1.525 |  |  |  | 25 | 0.0585 | 75 | 0.0683 | 1641 |  | Southwire | AAC : 1750 : Jessamine : 61
AAC | Cowslip | 2000 | 91 |  | 0.1482 |  |  | 1.63 |  |  |  | 25 | 0.0525 | 75 | 0.0609 | 1873 |  | Southwire | AAC : 2000 : Cowslip : 91
AAC | Lupine | 2500 | 91 |  | 0.1657 |  |  | 1.823 |  |  |  | 25 | 0.0446 | 75 | 0.0511 | 2365 |  | Southwire | AAC : 2500 : Lupine : 91
AAC | Trilium | 3000 | 127 |  | 0.1537 |  |  | 1.996 |  |  |  | 25 | 0.0392 | 75 | 0.0445 | 2840 |  | Southwire | AAC : 3000 : Trilium : 127
AAC | Bluebonnet | 3500 | 127 |  | 0.166 |  |  | 2.158 |  |  |  | 25 | 0.0355 | 75 | 0.0399 | 3345 |  | Southwire | AAC : 3500 : Bluebonnet : 127
AACSR | 266.8 - 26/7 | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.398 | 75 | 0.4656 | 250 | 115.6 | Southwire | AACSR : 266.8 : 266.8 - 26/7 : 26/7
AACSR | 266.8 - 30/7 | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.66 |  |  |  | 25 | 0.3946 | 75 | 0.4616 | 250.6 | 165.5 | Southwire | AACSR : 266.8 : 266.8 - 30/7 : 30/7
AACSR | 300.0 - 26/7 | 300 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.354 | 75 | 0.4142 | 281 | 129.8 | Southwire | AACSR : 300 : 300.0 - 26/7 : 26/7
AACSR | 336.4 - 26/7 | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.3158 | 75 | 0.3694 | 315 | 145.4 | Southwire | AACSR : 336.4 : 336.4 - 26/7 : 26/7
AACSR | 336.4 - 30/7 | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.3131 | 75 | 0.3663 | 316 | 208.7 | Southwire | AACSR : 336.4 : 336.4 - 30/7 : 30/7
AACSR | 397.5 - 26/7 | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2675 | 75 | 0.3128 | 372.2 | 171.9 | Southwire | AACSR : 397.5 : 397.5 - 26/7 : 26/7
AACSR | 397.5 - 30/7 | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2651 | 75 | 0.3101 | 373.3 | 246.5 | Southwire | AACSR : 397.5 : 397.5 - 30/7 : 30/7
AACSR | 477.0 - 26/7 | 477 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.2231 | 75 | 0.2608 | 446.7 | 206.4 | Southwire | AACSR : 477 : 477.0 - 26/7 : 26/7
AACSR | 477.0 - 30/7 | 477 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.2211 | 75 | 0.2586 | 448.1 | 295.9 | Southwire | AACSR : 477 : 477.0 - 30/7 : 30/7
AACSR | 556.5 - 26/7 | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1915 | 75 | 0.2238 | 521.5 | 241 | Southwire | AACSR : 556.5 : 556.5 - 26/7 : 26/7
AACSR | 556.5 - 30/7 | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.1897 | 75 | 0.2218 | 522.8 | 345.2 | Southwire | AACSR : 556.5 : 556.5 - 30/7 : 30/7
AACSR | 605.0 - 26/7 | 605 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1763 | 75 | 0.206 | 566.6 | 261.8 | Southwire | AACSR : 605 : 605.0 - 26/7 : 26/7
AACSR | 605.0 - 30/19 | 605 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1748 | 75 | 0.2043 | 568.2 | 367.4 | Southwire | AACSR : 605 : 605.0 - 30/19 : 30/19
AACSR | 605.0 - 30/7 | 605 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1746 | 75 | 0.2041 | 568.2 | 375.3 | Southwire | AACSR : 605 : 605.0 - 30/7 : 30/7
AACSR | 636.0 - 26/7 | 636 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.99 |  |  |  | 25 | 0.1678 | 75 | 0.196 | 596 | 275.2 | Southwire | AACSR : 636 : 636.0 - 26/7 : 26/7
AACSR | 636.0 - 30/19 | 636 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1663 | 75 | 0.1944 | 597.4 | 386.6 | Southwire | AACSR : 636 : 636.0 - 30/19 : 30/19
AACSR | 636.0 - 30/7 | 636 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1662 | 75 | 0.1942 | 597.4 | 394.5 | Southwire | AACSR : 636 : 636.0 - 30/7 : 30/7
AACSR | 666.6 - 26/7 | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1601 | 75 | 0.1871 | 624.5 | 288.5 | Southwire | AACSR : 666.6 : 666.6 - 26/7 : 26/7
AACSR | 715.5 - 26/7 | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1493 | 75 | 0.1744 | 670.6 | 309.7 | Southwire | AACSR : 715.5 : 715.5 - 26/7 : 26/7
AACSR | 715.5 - 30/19 | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1481 | 75 | 0.173 | 671.8 | 434 | Southwire | AACSR : 715.5 : 715.5 - 30/19 : 30/19
AACSR | 795.0 - 54/7 | 795 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1354 | 75 | 0.1625 | 744.5 | 273.8 | Southwire | AACSR : 795 : 795.0 - 54/7 : 54/7
AACSR | 795.0 - 45/7 | 795 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.167 | 75 | 0.1609 | 744.8 | 146.1 | Southwire | AACSR : 795 : 795.0 - 45/7 : 45/7
AACSR | 795.0 - 26/7 | 795 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1346 | 75 | 0.1572 | 745.3 | 344.2 | Southwire | AACSR : 795 : 795.0 - 26/7 : 26/7
AACSR | 795.0 - 30/19 | 795 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.1334 | 75 | 0.1558 | 746.9 | 483.1 | Southwire | AACSR : 795 : 795.0 - 30/19 : 30/19
AACSR | 795.0 - 30/7 | 795 | 30 | 7 | 0.1628 | 0.1628 | 0.4884 | 1.14 |  |  |  | 25 | 0.1333 | 75 | 0.1557 | 746.9 | 493.2 | Southwire | AACSR : 795 : 795.0 - 30/7 : 30/7
AACSR | 900.0 - 54/7 | 900 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.12 | 75 | 0.1437 | 843.4 | 310.2 | Southwire | AACSR : 900 : 900.0 - 54/7 : 54/7
AACSR | 900.0 - 45/7 | 900 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1214 | 75 | 0.1424 | 843.1 | 165.5 | Southwire | AACSR : 900 : 900.0 - 45/7 : 45/7
AACSR | 954.0 - 54/7 | 954 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.1133 | 75 | 0.1357 | 893.7 | 328.7 | Southwire | AACSR : 954 : 954.0 - 54/7 : 54/7
AACSR | 954.0 - 45/7 | 954 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.1148 | 75 | 0.1345 | 893.9 | 175.5 | Southwire | AACSR : 954 : 954.0 - 45/7 : 45/7
AACSR | 954.0 - 30/19 | 954 | 30 | 19 | 0.1783 | 0.107 | 0.535 | 1.248 |  |  |  | 25 | 0.1116 | 75 | 0.1302 | 895.9 | 579.5 | Southwire | AACSR : 954 : 954.0 - 30/19 : 30/19
AACSR | 1033.5 - 54/7 | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.246 |  |  |  | 25 | 0.1049 | 75 | 0.1254 | 967.8 | 356 | Southwire | AACSR : 1033.5 : 1033.5 - 54/7 : 54/7
AACSR | 1033.5 - 45/7 | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.1062 | 75 | 0.1244 | 967.8 | 189.8 | Southwire | AACSR : 1033.5 : 1033.5 - 45/7 : 45/7
AACSR | 1113.0 - 54/19 | 1113 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.0981 | 75 | 0.1172 | 1048.5 | 376.1 | Southwire | AACSR : 1113 : 1113.0 - 54/19 : 54/19
AACSR | 1113.0 - 45/7 | 1113 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.099 | 75 | 0.1158 | 1043.4 | 204.8 | Southwire | AACSR : 1113 : 1113.0 - 45/7 : 45/7
AACSR | 1192.5 - 54/19 | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.338 |  |  |  | 25 | 0.0918 | 75 | 0.1096 | 1122.8 | 402.7 | Southwire | AACSR : 1192.5 : 1192.5 - 54/19 : 54/19
AACSR | 1192.5 - 45/7 | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0927 | 75 | 0.1083 | 1117.6 | 219.1 | Southwire | AACSR : 1192.5 : 1192.5 - 45/7 : 45/7
AACSR | 1272.0 - 54/19 | 1272 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0864 | 75 | 0.1029 | 1198.1 | 429.3 | Southwire | AACSR : 1272 : 1272.0 - 54/19 : 54/19
AACSR | 1272.0 - 45/7 | 1272 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0872 | 75 | 0.1018 | 1191.6 | 233.9 | Southwire | AACSR : 1272 : 1272.0 - 45/7 : 45/7
AACSR | 1351.5 - 54/19 | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0815 | 75 | 0.097 | 1272.6 | 455.8 | Southwire | AACSR : 1351.5 : 1351.5 - 54/19 : 54/19
AACSR | 1351.5 - 45/7 | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0824 | 75 | 0.0961 | 1266.4 | 248.3 | Southwire | AACSR : 1351.5 : 1351.5 - 45/7 : 45/7
AACSR | 1431.0 - 54/19 | 1431 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0772 | 75 | 0.0918 | 1347.7 | 483.1 | Southwire | AACSR : 1431 : 1431.0 - 54/19 : 54/19
AACSR | 1431.0 - 45/7 | 1431 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0781 | 75 | 0.091 | 1340.5 | 263.1 | Southwire | AACSR : 1431 : 1431.0 - 45/7 : 45/7
AACSR | 1510.5 - 54/19 | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0734 | 75 | 0.0872 | 1421.5 | 509.2 | Southwire | AACSR : 1510.5 : 1510.5 - 54/19 : 54/19
AACSR | 1510.5 - 45/7 | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0743 | 75 | 0.0864 | 1415.2 | 277.4 | Southwire | AACSR : 1510.5 : 1510.5 - 45/7 : 45/7
AACSR | 1590.0 - 54/19 | 1590 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.545 |  |  |  | 25 | 0.07 | 75 | 0.083 | 1497.3 | 537 | Southwire | AACSR : 1590 : 1590.0 - 54/19 : 54/19
AACSR | 1590.0 - 45/7 | 1590 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0709 | 75 | 0.0824 | 1490.4 | 292.2 | Southwire | AACSR : 1590 : 1590.0 - 45/7 : 45/7
AACSR | 1780.0 - 84/19 | 1780 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.064 | 75 | 0.0739 | 1676.8 | 386.6 | Southwire | AACSR : 1780 : 1780.0 - 84/19 : 84/19
AACSR | 2034.5 - 72/7 | 2034.5 | 72 | 7 | 0.1681 | 0.1122 | 0.3366 | 1.681 |  |  |  | 25 | 0.0577 | 75 | 0.0663 | 1915.8 | 234.3 | Southwire | AACSR : 2034.5 : 2034.5 - 72/7 : 72/7
AACSR | 2057.0 - 76/19 | 2057 | 76 | 19 | 0.1645 | 0.0768 | 0.384 | 1.7 |  |  |  | 25 | 0.0569 | 75 | 0.0653 | 1936.5 | 298.5 | Southwire | AACSR : 2057 : 2057.0 - 76/19 : 76/19
AACSR | 2167.0 - 72/7 | 2167 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0547 | 75 | 0.0627 | 2040.8 | 249.1 | Southwire | AACSR : 2167 : 2167.0 - 72/7 : 72/7
AACSR | 2156.0 - 84/19 | 2156 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0541 | 75 | 0.0621 | 2029.9 | 467.4 | Southwire | AACSR : 2156 : 2156.0 - 84/19 : 84/19
AACSR | 2312.0 - 76/19 | 2312 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0516 | 75 | 0.0589 | 2176.6 | 335.4 | Southwire | AACSR : 2312 : 2312.0 - 76/19 : 76/19
AACSR | 2515.0 - 76/19 | 2515 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0481 | 75 | 0.0548 | 2367.9 | 364.8 | Southwire | AACSR : 2515 : 2515.0 - 76/19 : 76/19
AACTW | Logan/TW | 322.5 | 17 |  |  |  |  | 0.6 |  |  | 2 | 25 | 0.2898 | 75 | 0.3468 | 302.3 |  | Southwire | AACTW : 322.5 : Logan/TW : 17
AACTW | Tulip/TW | 336.4 | 17 |  |  |  |  | 0.612 |  |  | 2 | 25 | 0.2779 | 75 | 0.3325 | 315.3 |  | Southwire | AACTW : 336.4 : Tulip/TW : 17
AACTW | Canna/TW | 397.5 | 17 |  |  |  |  | 0.661 |  |  | 2 | 25 | 0.2355 | 75 | 0.2817 | 372.6 |  | Southwire | AACTW : 397.5 : Canna/TW : 17
AACTW | Wheeler/TW | 449.4 | 17 |  |  |  |  | 0.7 |  |  | 2 | 25 | 0.2087 | 75 | 0.2494 | 421.2 |  | Southwire | AACTW : 449.4 : Wheeler/TW : 17
AACTW | Cosmos/TW | 477 | 17 |  |  |  |  | 0.72 |  |  | 2 | 25 | 0.1968 | 75 | 0.2352 | 447.1 |  | Southwire | AACTW : 477 : Cosmos/TW : 17
AACTW | Zinnia/TW | 500 | 17 |  |  |  |  | 0.736 |  |  | 2 | 25 | 0.1879 | 75 | 0.2245 | 468.7 |  | Southwire | AACTW : 500 : Zinnia/TW : 17
AACTW | Mistletoe/TW | 556.5 | 17 |  |  |  |  | 0.775 |  |  | 2 | 25 | 0.1691 | 75 | 0.202 | 521.3 |  | Southwire | AACTW : 556.5 : Mistletoe/TW : 17
AACTW | Robson/TW | 595.8 | 17 |  |  |  |  | 0.8 |  |  | 2 | 25 | 0.1582 | 75 | 0.1888 | 558.4 |  | Southwire | AACTW : 595.8 : Robson/TW : 17
AACTW | Meadowsweet/TW | 600 | 17 |  |  |  |  | 0.803 |  |  | 2 | 25 | 0.1571 | 75 | 0.1875 | 562.4 |  | Southwire | AACTW : 600 : Meadowsweet/TW : 17
AACTW | Orchid/TW | 636 | 17 |  |  |  |  | 0.825 |  |  | 2 | 25 | 0.1485 | 75 | 0.1771 | 596.1 |  | Southwire | AACTW : 636 : Orchid/TW : 17
AACTW | Verbena/TW | 700 | 17 |  |  |  |  | 0.864 |  |  | 2 | 25 | 0.1353 | 75 | 0.1613 | 656.1 |  | Southwire | AACTW : 700 : Verbena/TW : 17
AACTW | Nasturtium/TW | 750 | 17 |  |  |  |  | 0.893 |  |  | 2 | 25 | 0.1266 | 75 | 0.1508 | 702.1 |  | Southwire | AACTW : 750 : Nasturtium/TW : 17
AACTW | McKinley/TW | 761.5 | 17 |  |  |  |  | 0.9 |  |  | 2 | 25 | 0.1247 | 75 | 0.1486 | 713.7 |  | Southwire | AACTW : 761.5 : McKinley/TW : 17
AACTW | Arbutus/TW | 795 | 17 |  |  |  |  | 0.919 |  |  | 2 | 25 | 0.1197 | 75 | 0.1425 | 745.1 |  | Southwire | AACTW : 795 : Arbutus/TW : 17
AACTW | Cockscomb/TW | 900 | 17 |  |  |  |  | 0.99 |  |  | 3 | 25 | 0.1064 | 75 | 0.1264 | 843.6 |  | Southwire | AACTW : 900 : Cockscomb/TW : 17
AACTW | Rainier/TW | 918.8 | 31 |  |  |  |  | 1 |  |  | 3 | 25 | 0.1043 | 75 | 0.1239 | 861.2 |  | Southwire | AACTW : 918.8 : Rainier/TW : 31
AACTW | Magnolia/TW | 954 | 31 |  |  |  |  | 1.018 |  |  | 3 | 25 | 0.1007 | 75 | 0.1195 | 894.2 |  | Southwire | AACTW : 954 : Magnolia/TW : 31
AACTW | Hawkweed/TW | 1000 | 31 |  |  |  |  | 1.041 |  |  | 3 | 25 | 0.0963 | 75 | 0.1142 | 937.3 |  | Southwire | AACTW : 1000 : Hawkweed/TW : 31
AACTW | Bluebell/TW | 1033.5 | 31 |  |  |  |  | 1.057 |  |  | 3 | 25 | 0.0934 | 75 | 0.1107 | 968.7 |  | Southwire | AACTW : 1033.5 : Bluebell/TW : 31
AACTW | Marigold/TW | 1113 | 31 |  |  |  |  | 1.095 |  |  | 3 | 25 | 0.0872 | 75 | 0.1032 | 1043.2 |  | Southwire | AACTW : 1113 : Marigold/TW : 31
AACTW | Helens/TW | 1123.1 | 31 |  |  |  |  | 1.1 |  |  | 3 | 25 | 0.0865 | 75 | 0.1023 | 1052.7 |  | Southwire | AACTW : 1123.1 : Helens/TW : 31
AACTW | Hawthorn/TW | 1192.5 | 31 |  |  |  |  | 1.132 |  |  | 3 | 25 | 0.0819 | 75 | 0.0967 | 1117.7 |  | Southwire | AACTW : 1192.5 : Hawthorn/TW : 31
AACTW | Narcissus/TW | 1272 | 31 |  |  |  |  | 1.168 |  |  | 3 | 25 | 0.0772 | 75 | 0.0911 | 1192.2 |  | Southwire | AACTW : 1272 : Narcissus/TW : 31
AACTW | Baker/TW | 1346.8 | 31 |  |  |  |  | 1.2 |  |  | 3 | 25 | 0.0734 | 75 | 0.0864 | 1262.3 |  | Southwire | AACTW : 1346.8 : Baker/TW : 31
AACTW | Columbine/TW | 1351.5 | 31 |  |  |  |  | 1.202 |  |  | 3 | 25 | 0.0731 | 75 | 0.0861 | 1266.3 |  | Southwire | AACTW : 1351.5 : Columbine/TW : 31
AACTW | Carnation/TW | 1431 | 31 |  |  |  |  | 1.236 |  |  | 3 | 25 | 0.0695 | 75 | 0.0817 | 1341.3 |  | Southwire | AACTW : 1431 : Carnation/TW : 31
AACTW | Hood/TW | 1583.2 | 34 |  |  |  |  | 1.3 |  |  | 3 | 25 | 0.0637 | 75 | 0.0746 | 1483.9 |  | Southwire | AACTW : 1583.2 : Hood/TW : 34
AACTW | Coreopsis/TW | 1590 | 49 |  |  |  |  | 1.315 |  |  | 4 | 25 | 0.0635 | 75 | 0.0743 | 1490.3 |  | Southwire | AACTW : 1590 : Coreopsis/TW : 49
AACTW | Jessamine/TW | 1750 | 49 |  |  |  |  | 1.377 |  |  | 4 | 25 | 0.0585 | 75 | 0.0683 | 1640.3 |  | Southwire | AACTW : 1750 : Jessamine/TW : 49
AACTW | Whitney/TW | 1812.7 | 49 |  |  |  |  | 1.4 |  |  | 4 | 25 | 0.0568 | 75 | 0.0662 | 1699 |  | Southwire | AACTW : 1812.7 : Whitney/TW : 49
AACTW | Cowslip/TW | 2000 | 49 |  |  |  |  | 1.468 |  |  | 4 | 25 | 0.0525 | 75 | 0.0609 | 1893 |  | Southwire | AACTW : 2000 : Cowslip/TW : 49
AACTW | Powell/TW | 2093.6 | 49 |  |  |  |  | 1.5 |  |  | 4 | 25 | 0.051 | 75 | 0.0591 | 1981.6 |  | Southwire | AACTW : 2093.6 : Powell/TW : 49
AACTW | Jefferson/TW | 2388.1 | 52 |  |  |  |  | 1.6 |  |  | 4 | 25 | 0.0461 | 75 | 0.053 | 2260.3 |  | Southwire | AACTW : 2388.1 : Jefferson/TW : 52
AACTW | Lupine/TW | 2500 | 71 |  |  |  |  | 1.648 |  |  | 5 | 25 | 0.0446 | 75 | 0.0511 | 2366.2 |  | Southwire | AACTW : 2500 : Lupine/TW : 71
AACTW | Trillium/TW | 3000 | 71 |  |  |  |  | 1.799 |  |  | 5 | 25 | 0.0392 | 75 | 0.0445 | 2839.5 |  | Southwire | AACTW : 3000 : Trillium/TW : 71
ACAR | 355 - 12/7 | 355 | 12 | 7 | 0.1367 | 0.1367 | 0.399 | 0.684 |  |  |  | 25 | 0.2776 | 75 | 0.3296 | 333 |  | Southwire | ACAR : 355 : 355 - 12/7 : 12/7
ACAR | 355 - 15/4 | 355 | 15 | 4 | 0.1367 | 0.1367 | 0.182 | 0.684 |  |  |  | 25 | 0.2714 | 75 | 0.3233 | 333.3 |  | Southwire | ACAR : 355 : 355 - 15/4 : 15/4
ACAR | 395.1 - 15/4 | 395.1 | 15 | 4 | 0.1442 | 0.1442 | 0.192 | 0.721 |  |  |  | 25 | 0.2441 | 75 | 0.2907 | 369.9 |  | Southwire | ACAR : 395.1 : 395.1 - 15/4 : 15/4
ACAR | 465.9 - 12/7 | 465.9 | 12 | 7 | 0.1566 | 0.1566 | 0.457 | 0.783 |  |  |  | 25 | 0.2121 | 75 | 0.2517 | 435.9 |  | Southwire | ACAR : 465.9 : 465.9 - 12/7 : 12/7
ACAR | 503.6 - 12/7 | 503.6 | 12 | 7 | 0.1628 | 0.1628 | 0.475 | 0.814 |  |  |  | 25 | 0.1965 | 75 | 0.233 | 471.1 |  | Southwire | ACAR : 503.6 : 503.6 - 12/7 : 12/7
ACAR | 503.6 - 15/4 | 503.6 | 15 | 4 | 0.1628 | 0.1628 | 0.217 | 0.814 |  |  |  | 25 | 0.1921 | 75 | 0.2286 | 471.5 |  | Southwire | ACAR : 503.6 : 503.6 - 15/4 : 15/4
ACAR | 559.5 - 15/4 | 559.5 | 15 | 4 | 0.1716 | 0.1716 | 0.229 | 0.858 |  |  |  | 25 | 0.1732 | 75 | 0.206 | 523.8 |  | Southwire | ACAR : 559.5 : 559.5 - 15/4 : 15/4
ACAR | 587.2 - 15/4 | 587.2 | 15 | 4 | 0.1758 | 0.1758 | 0.234 | 0.879 |  |  |  | 25 | 0.1652 | 75 | 0.1964 | 549.8 |  | Southwire | ACAR : 587.2 : 587.2 - 15/4 : 15/4
ACAR | 653.1 - 12/7 | 653.1 | 12 | 7 | 0.1854 | 0.1854 | 0.541 | 0.927 |  |  |  | 25 | 0.1523 | 75 | 0.1804 | 611 |  | Southwire | ACAR : 653.1 : 653.1 - 12/7 : 12/7
ACAR | 653.1 - 15/4 | 653.1 | 15 | 4 | 0.1854 | 0.1854 | 0.247 | 0.927 |  |  |  | 25 | 0.149 | 75 | 0.1769 | 611.5 |  | Southwire | ACAR : 653.1 : 653.1 - 15/4 : 15/4
ACAR | 739.8 - 18/19 | 739.8 | 18 | 19 | 0.1414 | 0.1414 | 1.045 | 0.99 |  |  |  | 25 | 0.1378 | 75 | 0.1625 | 691.6 |  | Southwire | ACAR : 739.8 : 739.8 - 18/19 : 18/19
ACAR | 739.8 - 24/13 | 739.8 | 24 | 13 | 0.1414 | 0.1414 | 0.536 | 0.99 |  |  |  | 25 | 0.1346 | 75 | 0.1593 | 692.1 |  | Southwire | ACAR : 739.8 : 739.8 - 24/13 : 24/13
ACAR | 739.8 - 30/7 | 739.8 | 30 | 7 | 0.1414 | 0.1414 | 0.231 | 0.99 |  |  |  | 25 | 0.1316 | 75 | 0.1562 | 692.7 |  | Southwire | ACAR : 739.8 : 739.8 - 30/7 : 30/7
ACAR | 739.8 - 33/4 | 739.8 | 33 | 4 | 0.1414 | 0.1414 | 0.12 | 0.99 |  |  |  | 25 | 0.1302 | 75 | 0.1547 | 693 |  | Southwire | ACAR : 739.8 : 739.8 - 33/4 : 33/4
ACAR | 853.7 - 18/19 | 853.7 | 18 | 19 | 0.1519 | 0.1519 | 1.122 | 1.063 |  |  |  | 25 | 0.1201 | 75 | 0.1414 | 798.1 |  | Southwire | ACAR : 853.7 : 853.7 - 18/19 : 18/19
ACAR | 853.7 - 24/13 | 853.7 | 24 | 13 | 0.1519 | 0.1519 | 0.576 | 1.063 |  |  |  | 25 | 0.1173 | 75 | 0.1386 | 798.7 |  | Southwire | ACAR : 853.7 : 853.7 - 24/13 : 24/13
ACAR | 853.7 - 30/7 | 853.7 | 30 | 7 | 0.1519 | 0.1519 | 0.248 | 1.063 |  |  |  | 25 | 0.1147 | 75 | 0.1359 | 799.4 |  | Southwire | ACAR : 853.7 : 853.7 - 30/7 : 30/7
ACAR | 927.2 - 18/19 | 927.2 | 18 | 19 | 0.1583 | 0.1583 | 1.17 | 1.108 |  |  |  | 25 | 0.111 | 75 | 0.1305 | 866.7 |  | Southwire | ACAR : 927.2 : 927.2 - 18/19 : 18/19
ACAR | 927.2 - 24/13 | 927.2 | 24 | 13 | 0.1583 | 0.1583 | 0.6 | 1.108 |  |  |  | 25 | 0.1084 | 75 | 0.128 | 867.5 |  | Southwire | ACAR : 927.2 : 927.2 - 24/13 : 24/13
ACAR | 927.2 - 30/7 | 927.2 | 30 | 7 | 0.1583 | 0.1583 | 0.259 | 1.108 |  |  |  | 25 | 0.1061 | 75 | 0.1255 | 868.2 |  | Southwire | ACAR : 927.2 : 927.2 - 30/7 : 30/7
ACAR | 1024.5 - 18/19 | 1024.5 | 18 | 19 | 0.1664 | 0.1664 | 1.23 | 1.165 |  |  |  | 25 | 0.101 | 75 | 0.1187 | 957.7 |  | Southwire | ACAR : 1024.5 : 1024.5 - 18/19 : 18/19
ACAR | 1024.5 - 24/13 | 1024.5 | 24 | 13 | 0.1664 | 0.1664 | 0.631 | 1.165 |  |  |  | 25 | 0.0987 | 75 | 0.1164 | 958.5 |  | Southwire | ACAR : 1024.5 : 1024.5 - 24/13 : 24/13
ACAR | 1024.5 - 30/7 | 1024.5 | 30 | 7 | 0.1664 | 0.1664 | 0.272 | 1.165 |  |  |  | 25 | 0.0966 | 75 | 0.1142 | 959.3 |  | Southwire | ACAR : 1024.5 : 1024.5 - 30/7 : 30/7
ACAR | 1081 - 18/19 | 1081 | 18 | 19 | 0.1709 | 0.1709 | 1.262 | 1.196 |  |  |  | 25 | 0.096 | 75 | 0.1127 | 1010.2 |  | Southwire | ACAR : 1081 : 1081 - 18/19 : 18/19
ACAR | 1081 - 24/13 | 1081 | 24 | 13 | 0.1709 | 0.1709 | 0.648 | 1.196 |  |  |  | 25 | 0.0939 | 75 | 0.1105 | 1011.1 |  | Southwire | ACAR : 1081 : 1081 - 24/13 : 24/13
ACAR | 1109 - 18/19 | 1109 | 18 | 19 | 0.1731 | 0.1731 | 1.279 | 1.212 |  |  |  | 25 | 0.0937 | 75 | 0.11 | 1036.4 |  | Southwire | ACAR : 1109 : 1109 - 18/19 : 18/19
ACAR | 1081 - 30/7 | 1081 | 30 | 7 | 0.1709 | 0.1709 | 0.279 | 1.196 |  |  |  | 25 | 0.0918 | 75 | 0.1084 | 1011.9 |  | Southwire | ACAR : 1081 : 1081 - 30/7 : 30/7
ACAR | 1109 - 24/13 | 1109 | 24 | 13 | 0.1731 | 0.1731 | 0.657 | 1.212 |  |  |  | 25 | 0.0917 | 75 | 0.1078 | 1037.2 |  | Southwire | ACAR : 1109 : 1109 - 24/13 : 24/13
ACAR | 1109 - 30/7 | 1109 | 30 | 7 | 0.1731 | 0.1731 | 0.283 | 1.212 |  |  |  | 25 | 0.0897 | 75 | 0.1058 | 1038.1 |  | Southwire | ACAR : 1109 : 1109 - 30/7 : 30/7
ACAR | 1172 - 18/19 | 1172 | 18 | 19 | 0.178 | 0.178 | 1.315 | 1.246 |  |  |  | 25 | 0.0891 | 75 | 0.1044 | 1095.9 |  | Southwire | ACAR : 1172 : 1172 - 18/19 : 18/19
ACAR | 1172 - 24/13 | 1172 | 24 | 13 | 0.178 | 0.178 | 0.675 | 1.246 |  |  |  | 25 | 0.0871 | 75 | 0.1024 | 1096.8 |  | Southwire | ACAR : 1172 : 1172 - 24/13 : 24/13
ACAR | 1197 - 18/19 | 1197 | 18 | 19 | 0.1799 | 0.1799 | 1.329 | 1.259 |  |  |  | 25 | 0.0873 | 75 | 0.1023 | 1119.4 |  | Southwire | ACAR : 1197 : 1197 - 18/19 : 18/19
ACAR | 1172 - 30/7 | 1172 | 30 | 7 | 0.178 | 0.178 | 0.291 | 1.246 |  |  |  | 25 | 0.0852 | 75 | 0.1004 | 1097.7 |  | Southwire | ACAR : 1172 : 1172 - 30/7 : 30/7
ACAR | 1197 - 24/13 | 1197 | 24 | 13 | 0.1799 | 0.1799 | 0.682 | 1.259 |  |  |  | 25 | 0.0854 | 75 | 0.1003 | 1120.3 |  | Southwire | ACAR : 1197 : 1197 - 24/13 : 24/13
ACAR | 1172 - 33/4 | 1172 | 33 | 4 | 0.178 | 0.178 | 0.151 | 1.246 |  |  |  | 25 | 0.0843 | 75 | 0.0995 | 1098.2 |  | Southwire | ACAR : 1172 : 1172 - 33/4 : 33/4
ACAR | 1197 - 30/7 | 1197 | 30 | 7 | 0.1799 | 0.1799 | 0.294 | 1.259 |  |  |  | 25 | 0.0836 | 75 | 0.0985 | 1121.3 |  | Southwire | ACAR : 1197 : 1197 - 30/7 : 30/7
ACAR | 1280 - 18/19 | 1280 | 18 | 19 | 0.186 | 0.186 | 1.374 | 1.302 |  |  |  | 25 | 0.0821 | 75 | 0.0961 | 1196.6 |  | Southwire | ACAR : 1280 : 1280 - 18/19 : 18/19
ACAR | 1280 - 24/13 | 1280 | 24 | 13 | 0.186 | 0.186 | 0.705 | 1.302 |  |  |  | 25 | 0.0803 | 75 | 0.0942 | 1197.6 |  | Southwire | ACAR : 1280 : 1280 - 24/13 : 24/13
ACAR | 1280 - 30/7 | 1280 | 30 | 7 | 0.186 | 0.186 | 0.304 | 1.302 |  |  |  | 25 | 0.0787 | 75 | 0.0925 | 1198.6 |  | Southwire | ACAR : 1280 : 1280 - 30/7 : 30/7
ACAR | 1362 - 54/7 | 1362 | 54 | 7 | 0.1494 | 0.1494 | 0.174 | 1.345 |  |  |  | 25 | 0.0737 | 75 | 0.0888 | 1275.4 |  | Southwire | ACAR : 1362 : 1362 - 54/7 : 54/7
ACAR | 1362 - 42/19 | 1362 | 42 | 19 | 0.1494 | 0.1494 | 0.608 | 1.345 |  |  |  | 25 | 0.0756 | 75 | 0.0886 | 1274.1 |  | Southwire | ACAR : 1362 : 1362 - 42/19 : 42/19
ACAR | 1703 - 54/7 | 1703 | 54 | 7 | 0.1671 | 0.1671 | 0.195 | 1.504 |  |  |  | 25 | 0.0607 | 75 | 0.0725 | 1595.5 |  | Southwire | ACAR : 1703 : 1703 - 54/7 : 54/7
ACAR | 1703 - 42/19 | 1703 | 42 | 19 | 0.1671 | 0.1671 | 0.68 | 1.504 |  |  |  | 25 | 0.0622 | 75 | 0.0723 | 1593.9 |  | Southwire | ACAR : 1703 : 1703 - 42/19 : 42/19
ACAR | 1703 - 48/13 | 1703 | 48 | 13 | 0.1671 | 0.1671 | 0.407 | 1.504 |  |  |  | 25 | 0.0614 | 75 | 0.0715 | 1594.7 |  | Southwire | ACAR : 1703 : 1703 - 48/13 : 48/13
ACAR | 1933 - 54/7 | 1933 | 54 | 7 | 0.178 | 0.178 | 0.208 | 1.602 |  |  |  | 25 | 0.0546 | 75 | 0.0648 | 1810.4 |  | Southwire | ACAR : 1933 : 1933 - 54/7 : 54/7
ACAR | 1933 - 42/19 | 1933 | 42 | 19 | 0.178 | 0.178 | 0.725 | 1.602 |  |  |  | 25 | 0.0559 | 75 | 0.0647 | 1808.6 |  | Southwire | ACAR : 1933 : 1933 - 42/19 : 42/19
ACAR | 1933 - 48/13 | 1933 | 48 | 13 | 0.178 | 0.178 | 0.434 | 1.602 |  |  |  | 25 | 0.0553 | 75 | 0.0641 | 1809.5 |  | Southwire | ACAR : 1933 : 1933 - 48/13 : 48/13
ACAR | 2267 - 42/19 | 2267 | 42 | 19 | 0.1928 | 0.1928 | 0.785 | 1.735 |  |  |  | 25 | 0.0496 | 75 | 0.0571 | 2142.7 |  | Southwire | ACAR : 2267 : 2267 - 42/19 : 42/19
ACAR | 2267 - 54/7 | 2267 | 54 | 7 | 0.1928 | 0.1928 | 0.225 | 1.735 |  |  |  | 25 | 0.0486 | 75 | 0.0571 | 2144.9 |  | Southwire | ACAR : 2267 : 2267 - 54/7 : 54/7
ACAR | 2267 - 48/13 | 2267 | 48 | 13 | 0.1928 | 0.1928 | 0.47 | 1.735 |  |  |  | 25 | 0.0491 | 75 | 0.0565 | 2143.8 |  | Southwire | ACAR : 2267 : 2267 - 48/13 : 48/13
ACAR | 2338 - 54/7 | 2338 | 54 | 7 | 0.1958 | 0.1958 | 0.228 | 1.762 |  |  |  | 25 | 0.0474 | 75 | 0.0557 | 2212.1 |  | Southwire | ACAR : 2338 : 2338 - 54/7 : 54/7
ACAR | 2338 - 42/19 | 2338 | 42 | 19 | 0.1958 | 0.1958 | 0.797 | 1.762 |  |  |  | 25 | 0.0484 | 75 | 0.0556 | 2209.9 |  | Southwire | ACAR : 2338 : 2338 - 42/19 : 42/19
ACAR | 2338 - 48/13 | 2338 | 48 | 13 | 0.1958 | 0.1958 | 0.477 | 1.762 |  |  |  | 25 | 0.0479 | 75 | 0.0551 | 2211 |  | Southwire | ACAR : 2338 : 2338 - 48/13 : 48/13
ACAR |  | 2493 | 54 | 37 | 0.19576 |  |  | 1.821 |  |  |  | 25 | 0.045936 | 75 | 0.0528 | 2363 |  | Alcan | ACAR : 2493 : : 54/37
ACCC | HAWK | 611 | [5 empty] | 0.858 |  |  |  | 25 | 0.14942 | 75 | 0.17952 | 624 |  | TransPower | ACCC : 611 : HAWK
ACCC | DOVE | 713 | [5 empty] | 0.927 |  |  |  | 25 | 0.1283 | 75 | 0.15418 | 728 |  | TransPower | ACCC : 713 : DOVE
ACCC | GROSBEAK | 816 | [5 empty] | 0.99 |  |  |  | 25 | 0.11299 | 75 | 0.13517 | 832 |  | TransPower | ACCC : 816 : GROSBEAK
ACCC | DRAKE | 1020 | [5 empty] | 1.108 |  |  |  | 25 | 0.090816 | 75 | 0.10877 | 1046 |  | TransPower | ACCC : 1020 : DRAKE
ACCC | CARDINAL | 1222 | [5 empty] | 1.196 |  |  |  | 25 | 0.077088 | 75 | 0.091872 | 1228 |  | TransPower | ACCC : 1222 : CARDINAL
ACCC | BITTERN | 1572 | [5 empty] | 1.345 |  |  |  | 25 | 0.061248 | 75 | 0.072864 | 1554 |  | TransPower | ACCC : 1572 : BITTERN
ACCC | LAPWING | 1966 | [5 empty] | 1.504 |  |  |  | 25 | 0.051005 | 75 | 0.059664 | 1960 |  | TransPower | ACCC : 1966 : LAPWING
ACCC | CHUKAR | 2242 | [5 empty] | 1.602 |  |  |  | 25 | 0.045883 | 75 | 0.053328 | 2225 |  | TransPower | ACCC : 2242 : CHUKAR
ACCR | 195-T20 | 195 | 7 | 7 | 0.167 | 0.074 | 0.222 | 0.556 |  | 20 | 1 | 25 | 0.4513 | 75 | 0.5405 | 183.3 | 45.7 | Southwire | ACCR : 195 : 195-T20 : 7/7
ACCR | 207-T23 | 207 | 30 | 7 | 0.083 | 0.083 | 0.249 | 0.582 |  | 23 | 2 | 25 | 0.4187 | 75 | 0.5015 | 195.6 | 57.2 | Southwire | ACCR : 207 : 207-T23 : 30/7
ACCR | Partridge | 257 | 26 | 7 | 0.1 | 0.077 | 0.232 | 0.63 |  | 16 | 2 | 25 | 0.3468 | 75 | 0.4145 | 242.5 | 49.8 | Southwire | ACCR : 257 : Partridge : 26/7
ACCR | Junco | 267 | 30 | 7 | 0.094 | 0.094 | 0.283 | 0.66 |  | 23 | 2 | 25 | 0.3253 | 75 | 0.3896 | 251.8 | 73.4 | Southwire | ACCR : 267 : Junco : 30/7
ACCR | Ostrich | 297 | 26 | 7 | 0.107 | 0.083 | 0.249 | 0.677 |  | 16 | 2 | 25 | 0.3004 | 75 | 0.3597 | 279.5 | 57.2 | Southwire | ACCR : 297 : Ostrich : 26/7
ACCR | Linnet | 340 | 26 | 7 | 0.114 | 0.089 | 0.267 | 0.724 |  | 16 | 2 | 25 | 0.2626 | 75 | 0.3144 | 319.8 | 65.3 | Southwire | ACCR : 340 : Linnet : 26/7
ACCR | Brant | 373 | 24 | 7 | 0.125 | 0.083 | 0.249 | 0.748 |  | 13 | 2 | 25 | 0.2427 | 75 | 0.2905 | 351.2 | 57.2 | Southwire | ACCR : 373 : Brant : 24/7
ACCR | Ibis | 382 | 26 | 7 | 0.121 | 0.094 | 0.283 | 0.768 |  | 16 | 2 | 25 | 0.2335 | 75 | 0.2796 | 360 | 73.4 | Southwire | ACCR : 382 : Ibis : 26/7
ACCR | Lark | 400 | 30 | 7 | 0.116 | 0.116 | 0.347 | 0.809 |  | 23 | 2 | 25 | 0.2171 | 75 | 0.2599 | 377.9 | 109.5 | Southwire | ACCR : 400 : Lark : 30/7
ACCR | 427-T13 | 427 | 24 | 7 | 0.133 | 0.089 | 0.267 | 0.8 |  | 13 | 2 | 25 | 0.2123 | 75 | 0.254 | 402 | 65.3 | Southwire | ACCR : 427 : 427-T13 : 24/7
ACCR | Hawk | 470 | 26 | 7 | 0.134 | 0.105 | 0.314 | 0.852 |  | 16 | 2 | 25 | 0.1901 | 75 | 0.2274 | 442.9 | 90.1 | Southwire | ACCR : 470 : Hawk : 26/7
ACCR | Flicker | 480 | 24 | 7 | 0.141 | 0.094 | 0.283 | 0.849 |  | 13 | 2 | 25 | 0.1888 | 75 | 0.2259 | 452.3 | 73.4 | Southwire | ACCR : 480 : Flicker : 24/7
ACCR | Dove | 573 | 26 | 7 | 0.149 | 0.116 | 0.347 | 0.941 |  | 16 | 2 | 25 | 0.1562 | 75 | 0.1868 | 540 | 109.5 | Southwire | ACCR : 573 : Dove : 26/7
ACCR | Peacock | 591 | 24 | 7 | 0.157 | 0.105 | 0.314 | 0.941 |  | 13 | 2 | 25 | 0.1539 | 75 | 0.1839 | 556.5 | 90.1 | Southwire | ACCR : 591 : Peacock : 24/7
ACCR | Eagle | 575 | 30 | 19 | 0.139 | 0.083 | 0.416 | 0.97 |  | 23 | 2 | 25 | 0.1517 | 75 | 0.1815 | 543.3 | 153.4 | Southwire | ACCR : 575 : Eagle : 30/19
ACCR | Goldfinch | 634 | 22 | 7 | 0.17 | 0.094 | 0.283 | 0.962 |  | 10 | 2 | 25 | 0.1456 | 75 | 0.174 | 597 | 73.4 | Southwire | ACCR : 634 : Goldfinch : 22/7
ACCR | Grosbeak | 656 | 26 | 19 | 0.159 | 0.074 | 0.371 | 1.006 |  | 16 | 2 | 25 | 0.1371 | 75 | 0.1638 | 617.4 | 122.3 | Southwire | ACCR : 656 : Grosbeak : 26/19
ACCR | 680-T19 | 680 | 28 | 19 | 0.156 | 0.083 | 0.416 | 1.039 |  | 19 | 2 | 25 | 0.1307 | 75 | 0.1561 | 641.8 | 153.4 | Southwire | ACCR : 680 : 680-T19 : 28/19
ACCR | Stilt | 720 | 24 | 7 | 0.173 | 0.116 | 0.347 | 1.04 |  | 13 | 2 | 25 | 0.1266 | 75 | 0.1512 | 678.5 | 109.5 | Southwire | ACCR : 720 : Stilt : 24/7
ACCR | Puffin | 780 | 22 | 7 | 0.188 | 0.105 | 0.314 | 1.067 |  | 10 | 2 | 25 | 0.1189 | 75 | 0.1418 | 734.6 | 90.1 | Southwire | ACCR : 780 : Puffin : 22/7
ACCR | Condor | 795 | 24 | 19 | 0.185 | 0.074 | 0.371 | 1.112 |  | 13 | 2 | 25 | 0.1112 | 75 | 0.1327 | 775.8 | 122.3 | Southwire | ACCR : 795 : Condor : 24/19
ACCR | Drake | 824 | 26 | 19 | 0.178 | 0.083 | 0.416 | 1.128 |  | 16 | 2 | 25 | 0.1095 | 75 | 0.1307 | 776.5 | 153.4 | Southwire | ACCR : 824 : Drake : 26/19
ACCR | 951-T10 | 951 | 22 | 7 | 0.208 | 0.116 | 0.347 | 1.178 |  | 10 | 2 | 25 | 0.0981 | 75 | 0.1168 | 895.6 | 109.5 | Southwire | ACCR : 951 : 951-T10 : 22/7
ACCR | Curlew | 1036 | 54 | 19 | 0.139 | 0.083 | 0.416 | 1.247 |  | 13 | 3 | 25 | 0.0895 | 75 | 0.1066 | 980.4 | 153.4 | Southwire | ACCR : 1036 : Curlew : 54/19
ACCR | Bittern | 1238 | 51 | 19 | 0.156 | 0.083 | 0.416 | 1.35 |  | 11 | 3 | 25 | 0.0764 | 75 | 0.0906 | 1179.9 | 153.4 | Southwire | ACCR : 1238 : Bittern : 51/19
ACCR | Martin | 1334 | 54 | 19 | 0.157 | 0.094 | 0.472 | 1.415 |  | 13 | 3 | 25 | 0.0705 | 75 | 0.0836 | 1262.5 | 197.1 | Southwire | ACCR : 1334 : Martin : 54/19
ACCR | Lapwing | 1594 | 51 | 19 | 0.177 | 0.094 | 0.472 | 1.532 |  | 11 | 3 | 25 | 0.0605 | 75 | 0.0714 | 1509.1 | 197.1 | Southwire | ACCR : 1594 : Lapwing : 51/19
ACCR | Falcon | 1641 | 54 | 19 | 0.174 | 0.105 | 0.523 | 1.569 |  | 13 | 3 | 25 | 0.0583 | 75 | 0.0688 | 1553.3 | 242.1 | Southwire | ACCR : 1641 : Falcon : 54/19
ACCR | 1851-T13 | 1851 | 54 | 19 | 0.185 | 0.111 | 0.556 | 1.667 |  | 13 | 3 | 25 | 0.0523 | 75 | 0.0615 | 1752.4 | 272.8 | Southwire | ACCR : 1851 : 1851-T13 : 54/19
ACCRTW | Hawk/TW | 477 | 18 | 7 | 0.163 | 0.105 | 0.314 | 0.789 |  | 16 | 2 | 25 | 0.187 | 75 | 0.2238 | 447.6 | 90.4 | Southwire | ACCRTW : 477 : Hawk/TW : 18/7
ACCRTW | Calumet/TW | 565 | 20 | 7 | 0.1681 | 0.116 | 0.347 | 0.861 |  | 17 | 2 | 25 | 0.1578 | 75 | 0.1888 | 530.2 | 109.9 | Southwire | ACCRTW : 565 : Calumet/TW : 20/7
ACCRTW | Oswego/TW | 665 | 20 | 19 | 0.182 | 0.074 | 0.371 | 0.919 |  | 16 | 2 | 25 | 0.1348 | 75 | 0.1612 | 624 | 122.7 | Southwire | ACCRTW : 665 : Oswego/TW : 20/19
ACCRTW | Wabash/TW | 763 | 20 | 19 | 0.195 | 0.083 | 0.416 | 0.99 |  | 17 | 2 | 25 | 0.117 | 75 | 0.1398 | 716 | 153.9 | Southwire | ACCRTW : 763 : Wabash/TW : 20/19
ACCRTW | Condor/TW | 795 | 20 | 19 | 0.1994 | 0.0741 | 0.371 | 0.995 |  | 13 | 2 | 25 | 0.1145 | 75 | 0.1367 | 746 | 122.7 | Southwire | ACCRTW : 795 : Condor/TW : 20/19
ACCRTW | Suwanee/TW | 958 | 24 | 19 | 0.1998 | 0.089 | 0.445 | 1.1099 |  | 16 | 2 | 25 | 0.0943 | 75 | 0.1125 | 899 | 175.9 | Southwire | ACCRTW : 958 : Suwanee/TW : 24/19
ACCRTW | Curlew/TW | 1033 | 20 | 19 | 0.2273 | 0.083 | 0.416 | 1.132 |  | 13 | 2 | 25 | 0.0889 | 75 | 0.1059 | 969.4 | 153.9 | Southwire | ACCRTW : 1033 : Curlew/TW : 20/19
ACCRTW | 1033-T23/TW | 1033 | 24 | 19 | 0.2075 | 0.111 | 0.556 | 1.189 |  | 23 | 2 | 25 | 0.085 | 75 | 0.1013 | 969.4 | 273.8 | Southwire | ACCRTW : 1033 : 1033-T23/TW : 24/19
ACCRTW | Hudson/TW | 1158 | 22 | 19 | 0.229 | 0.089 | 0.445 | 1.199 |  | 13 | 2 | 25 | 0.0796 | 75 | 0.0947 | 1086.7 | 175.9 | Southwire | ACCRTW : 1158 : Hudson/TW : 22/19
ACCRTW | Pecos/TW | 1622 | 38 | 19 | 0.2067 | 0.105 | 0.523 | 1.411 |  | 13 | 3 | 25 | 0.0584 | 75 | 0.069 | 1531 | 242.9 | Southwire | ACCRTW : 1622 : Pecos/TW : 38/19
ACCRTW | Cumberland/TW | 1927 | 42 | 19 | 0.2142 | 0.116 | 0.578 | 1.551 |  | 13 | 3 | 25 | 0.0499 | 75 | 0.0587 | 1818.9 | 295.7 | Southwire | ACCRTW : 1927 : Cumberland/TW : 42/19
ACSR | Turkey | 6 | 6 | 1 | 0.0661 | 0.0661 | 0.0661 | 0.198 | 2.66 |  |  | 25 | 3.454 | 75 | 4.32 | 24.5 | 11.6 | Southwire | ACSR : 6 : Turkey : 6/1
ACSR | Swanate | 4 | 7 | 1 | 0.0772 | 0.1029 | 0.1029 | 0.257 | 3.45 |  |  | 25 | 2.147 | 75 | 2.779 | 38.9 | 28 | Southwire | ACSR : 4 : Swanate : 7/1
ACSR | Swan | 4 | 6 | 1 | 0.0834 | 0.0834 | 0.0834 | 0.25 | 3.35 |  |  | 25 | 2.172 | 75 | 2.765 | 38.9 | 18.4 | Southwire | ACSR : 4 : Swan : 6/1
ACSR | Sparate | 2 | 7 | 1 | 0.0974 | 0.1299 | 0.1299 | 0.325 | 4.35 |  |  | 25 | 1.351 | 75 | 1.787 | 61.9 | 44.7 | Southwire | ACSR : 2 : Sparate : 7/1
ACSR | Sparrow | 2 | 6 | 1 | 0.1052 | 0.1052 | 0.1052 | 0.316 | 4.23 |  |  | 25 | 1.366 | 75 | 1.778 | 61.9 | 29.3 | Southwire | ACSR : 2 : Sparrow : 6/1
ACSR | Grouse | 80 | 8 | 1 | 0.1 | 0.167 | 0.167 | 0.367 | 4.77 |  |  | 25 | 1.112 | 75 | 1.525 | 75 | 73.9 | Southwire | ACSR : 80 : Grouse : 8/1
ACSR | Robin | 1 | 6 | 1 | 0.1181 | 0.1182 | 0.1182 | 0.355 | 4.75 |  |  | 25 | 1.083 | 75 | 1.427 | 78.1 | 37 | Southwire | ACSR : 1 : Robin : 6/1
ACSR | Petrel | 101.8 | 12 | 7 | 0.0921 | 0.0921 | 0.2763 | 0.461 | 5.76 |  |  | 25 | 0.853 | 75 | 1.321 | 95.9 | 157.9 | Southwire | ACSR : 101.8 : Petrel : 12/7
ACSR | Minorca | 110.8 | 12 | 7 | 0.0961 | 0.0961 | 0.2883 | 0.481 | 6.01 |  |  | 25 | 0.783 | 75 | 1.233 | 104.4 | 171.9 | Southwire | ACSR : 110.8 : Minorca : 12/7
ACSR | Raven | 1/0 | 6 | 1 | 0.1327 | 0.1327 | 0.1327 | 0.398 | 5.33 |  |  | 25 | 0.859 | 75 | 1.145 | 98.5 | 46.6 | Southwire | ACSR : 1/0 : Raven : 6/1
ACSR | Leghorn | 134.6 | 12 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.53 | 6.62 |  |  | 25 | 0.645 | 75 | 1.053 | 126.8 | 208.7 | Southwire | ACSR : 134.6 : Leghorn : 12/7
ACSR | Quail | 2/0 | 6 | 1 | 0.1489 | 0.1489 | 0.1489 | 0.447 | 5.99 |  |  | 25 | 0.681 | 75 | 0.924 | 124.1 | 58.7 | Southwire | ACSR : 2/0 : Quail : 6/1
ACSR | Guinea | 159 | 12 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.576 | 7.19 |  |  | 25 | 0.491 | 75 | 0.921 | 149.7 | 246.6 | Southwire | ACSR : 159 : Guinea : 12/7
ACSR | Pigeon | 3/0 | 6 | 1 | 0.1672 | 0.1672 | 0.1672 | 0.502 | 6.72 |  |  | 25 | 0.541 | 75 | 0.746 | 156.4 | 74 | Southwire | ACSR : 3/0 : Pigeon : 6/1
ACSR | Cochin | 211.3 | 12 | 7 | 0.1327 | 0.1327 | 0.3981 | 0.664 | 8.29 |  |  | 25 | 0.411 | 75 | 0.732 | 199 | 327.8 | Southwire | ACSR : 211.3 : Cochin : 12/7
ACSR | Penguin | 4/0 | 6 | 1 | 0.1878 | 0.1878 | 0.1878 | 0.563 | 7.55 |  |  | 25 | 0.429 | 75 | 0.602 | 197.4 | 93.4 | Southwire | ACSR : 4/0 : Penguin : 6/1
ACSR | Waxwing | 266.8 | 18 | 1 | 0.1217 | 0.1217 | 0.1217 | 0.609 |  |  |  | 25 | 0.3471 | 75 | 0.4155 | 249.9 | 39.2 | Southwire | ACSR : 266.8 : Waxwing : 18/1
ACSR | Partridge | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3437 | 75 | 0.4113 | 251.3 | 115.6 | Southwire | ACSR : 266.8 : Partridge : 26/7
ACSR | Junco | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.66 |  |  |  | 25 | 0.3413 | 75 | 0.4083 | 251.9 | 165.5 | Southwire | ACSR : 266.8 : Junco : 30/7
ACSR | Ostrich | 300 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.3058 | 75 | 0.3659 | 282.5 | 129.7 | Southwire | ACSR : 300 : Ostrich : 26/7
ACSR | Merlin | 336.4 | 18 | 1 | 0.1367 | 0.1367 | 0.1367 | 0.684 |  |  |  | 25 | 0.2756 | 75 | 0.3298 | 315.3 | 49.5 | Southwire | ACSR : 336.4 : Merlin : 18/1
ACSR | Widgeon | 336.4 | 24 | 7 | 0.1184 | 0.0789 | 0.2367 | 0.7103 |  |  |  | 25 | 0.274 | 75 | 0.3279 | 316.9 | 115.9 | Southwire | ACSR : 336.4 : Widgeon : 24/7
ACSR | Linnet | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.2728 | 75 | 0.3264 | 316.6 | 145.4 | Southwire | ACSR : 336.4 : Linnet : 26/7
ACSR | Oriole | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2708 | 75 | 0.324 | 317.7 | 208.7 | Southwire | ACSR : 336.4 : Oriole : 30/7
ACSR | Chickadee | 397.5 | 18 | 1 | 0.1486 | 0.1486 | 0.1486 | 0.743 |  |  |  | 25 | 0.2336 | 75 | 0.2794 | 372.5 | 58.5 | Southwire | ACSR : 397.5 : Chickadee : 18/1
ACSR | Brant | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2321 | 75 | 0.2777 | 374.4 | 137 | Southwire | ACSR : 397.5 : Brant : 24/7
ACSR | Ibis | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2311 | 75 | 0.2764 | 374.1 | 171.9 | Southwire | ACSR : 397.5 : Ibis : 26/7
ACSR | Lark | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2294 | 75 | 0.2743 | 375.3 | 246.5 | Southwire | ACSR : 397.5 : Lark : 30/7
ACSR | Pelican | 477 | 18 | 1 | 0.1628 | 0.1628 | 0.1628 | 0.814 |  |  |  | 25 | 0.195 | 75 | 0.2331 | 447.1 | 70.2 | Southwire | ACSR : 477 : Pelican : 18/1
ACSR | Flicker | 477 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1937 | 75 | 0.2316 | 449.4 | 164.5 | Southwire | ACSR : 477 : Flicker : 24/7
ACSR | Hawk | 477 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1928 | 75 | 0.2305 | 449 | 206.4 | Southwire | ACSR : 477 : Hawk : 26/7
ACSR | Hen | 477 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.1913 | 75 | 0.2288 | 450.4 | 296 | Southwire | ACSR : 477 : Hen : 30/7
ACSR | Osprey | 556.5 | 18 | 1 | 0.1758 | 0.1758 | 0.1758 | 0.879 |  |  |  | 25 | 0.1676 | 75 | 0.2002 | 521.4 | 81.8 | Southwire | ACSR : 556.5 : Osprey : 18/1
ACSR | Parakeet | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.1663 | 75 | 0.1988 | 524.3 | 191.8 | Southwire | ACSR : 556.5 : Parakeet : 24/7
ACSR | Dove | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1655 | 75 | 0.1978 | 524.2 | 241 | Southwire | ACSR : 556.5 : Dove : 26/7
ACSR | Eagle | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.1642 | 75 | 0.1963 | 525.4 | 345.2 | Southwire | ACSR : 556.5 : Eagle : 30/7
ACSR | Duck | 605 | 54 | 7 | 0.1058 | 0.1058 | 0.3174 | 0.952 |  |  |  | 25 | 0.1533 | 75 | 0.188 | 569.3 | 208.3 | Southwire | ACSR : 605 : Duck : 54/7
ACSR | Peacock | 605 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.1532 | 75 | 0.183 | 570.1 | 208.7 | Southwire | ACSR : 605 : Peacock : 24/7
ACSR | Squab | 605 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1524 | 75 | 0.1821 | 569.5 | 261.8 | Southwire | ACSR : 605 : Squab : 26/7
ACSR | Teal | 605 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1513 | 75 | 0.1808 | 571.2 | 367.4 | Southwire | ACSR : 605 : Teal : 30/19
ACSR | Wood Duck | 605 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1512 | 75 | 0.1806 | 571.2 | 375.3 | Southwire | ACSR : 605 : Wood Duck : 30/7
ACSR | Goose | 636 | 54 | 7 | 0.1085 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1459 | 75 | 0.1789 | 598.8 | 219.1 | Southwire | ACSR : 636 : Goose : 54/7
ACSR | Swift | 636 | 36 | 1 | 0.1329 | 0.1329 | 0.1329 | 0.93 |  |  |  | 25 | 0.1477 | 75 | 0.1763 | 596 | 46.8 | Southwire | ACSR : 636 : Swift : 36/1
ACSR | Kingbird | 636 | 18 | 1 | 0.188 | 0.188 | 0.188 | 0.94 |  |  |  | 25 | 0.147 | 75 | 0.1755 | 596.3 | 93.6 | Southwire | ACSR : 636 : Kingbird : 18/1
ACSR | Rook | 636 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1458 | 75 | 0.1742 | 599.1 | 219.1 | Southwire | ACSR : 636 : Rook : 24/7
ACSR | Grosbeak | 636 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.99 |  |  |  | 25 | 0.1451 | 75 | 0.1733 | 599 | 275.2 | Southwire | ACSR : 636 : Grosbeak : 26/7
ACSR | Egret | 636 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.144 | 75 | 0.172 | 600.5 | 386.7 | Southwire | ACSR : 636 : Egret : 30/19
ACSR | Scoter | 636 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1439 | 75 | 0.1719 | 600.5 | 394.6 | Southwire | ACSR : 636 : Scoter : 30/7
ACSR | Gull | 666.6 | 54 | 7 | 0.1111 | 0.1111 | 0.3333 | 0.9999 |  |  |  | 25 | 0.1394 | 75 | 0.1708 | 627.8 | 229.7 | Southwire | ACSR : 666.6 : Gull : 54/7
ACSR | Flamingo | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1 |  |  |  | 25 | 0.1393 | 75 | 0.1663 | 628.2 | 229.7 | Southwire | ACSR : 666.6 : Flamingo : 24/7
ACSR | Gannet | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1385 | 75 | 0.1654 | 627.7 | 288.5 | Southwire | ACSR : 666.6 : Gannet : 26/7
ACSR | Crow | 715.5 | 54 | 7 | 0.1151 | 0.1151 | 0.345 | 1.04 |  |  |  | 25 | 0.1299 | 75 | 0.1592 | 673.8 | 246.5 | Southwire | ACSR : 715.5 : Crow : 54/7
ACSR | Stilt | 715.5 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.036 |  |  |  | 25 | 0.1299 | 75 | 0.1551 | 674.2 | 246.6 | Southwire | ACSR : 715.5 : Stilt : 24/7
ACSR | Starling | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1292 | 75 | 0.1543 | 674 | 309.7 | Southwire | ACSR : 715.5 : Starling : 26/7
ACSR | Redwing | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1282 | 75 | 0.1531 | 675.3 | 434 | Southwire | ACSR : 715.5 : Redwing : 30/19
ACSR | Condor | 795 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1172 | 75 | 0.1434 | 748.4 | 273.9 | Southwire | ACSR : 795 : Condor : 54/7
ACSR | Tern | 795 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1185 | 75 | 0.1421 | 748.6 | 146.1 | Southwire | ACSR : 795 : Tern : 45/7
ACSR | Coot | 795 | 36 | 1 | 0.1486 | 0.1486 | 0.1486 | 1.04 |  |  |  | 25 | 0.119 | 75 | 0.1417 | 745.1 | 58.5 | Southwire | ACSR : 795 : Coot : 36/1
ACSR | Turbit | 795 | 20 | 7 | 0.1994 | 0.0886 | 0.2658 | 1.0634 |  |  |  | 25 | 0.1185 | 75 | 0.1412 | 749 | 146.1 | Southwire | ACSR : 795 : Turbit : 20/7
ACSR | Puffin | 795 | 22 | 7 | 0.1901 | 0.1056 | 0.3168 | 1.0772 |  |  |  | 25 | 0.1179 | 75 | 0.1405 | 748.8 | 207.6 | Southwire | ACSR : 795 : Puffin : 22/7
ACSR | Cuckoo | 795 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1172 | 75 | 0.1398 | 748.8 | 273.9 | Southwire | ACSR : 795 : Cuckoo : 24/7
ACSR | Drake | 795 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1166 | 75 | 0.139 | 749.1 | 344.3 | Southwire | ACSR : 795 : Drake : 26/7
ACSR | Mallard | 795 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.1156 | 75 | 0.138 | 750.7 | 483.2 | Southwire | ACSR : 795 : Mallard : 30/19
ACSR | Skimmer | 795 | 30 | 7 | 0.1628 | 0.1628 | 0.4884 | 1.14 |  |  |  | 25 | 0.1155 | 75 | 0.1379 | 750.7 | 493.3 | Southwire | ACSR : 795 : Skimmer : 30/7
ACSR | Canary | 900 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1039 | 75 | 0.1269 | 847.7 | 310.2 | Southwire | ACSR : 900 : Canary : 54/7
ACSR | Ruddy | 900 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1051 | 75 | 0.1259 | 847.4 | 165.5 | Southwire | ACSR : 900 : Ruddy : 45/7
ACSR | Cardinal | 954 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0982 | 75 | 0.1199 | 898.3 | 328.7 | Southwire | ACSR : 954 : Cardinal : 54/7
ACSR | Rail | 954 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0994 | 75 | 0.1189 | 898.5 | 175.5 | Southwire | ACSR : 954 : Rail : 45/7
ACSR | Corncrake | 954 | 20 | 7 | 0.2184 | 0.0971 | 0.291 | 1.165 |  |  |  | 25 | 0.0994 | 75 | 0.1183 | 898.5 | 175.5 | Southwire | ACSR : 954 : Corncrake : 20/7
ACSR | Redbird | 954 | 24 | 7 | 0.1994 | 0.1329 | 0.399 | 1.196 |  |  |  | 25 | 0.0982 | 75 | 0.117 | 898.8 | 328.7 | Southwire | ACSR : 954 : Redbird : 24/7
ACSR | Merganser | 954 | 30 | 7 | 0.1783 | 0.1783 | 0.5349 | 1.2481 |  |  |  | 25 | 0.0967 | 75 | 0.1152 | 900.5 | 591.7 | Southwire | ACSR : 954 : Merganser : 30/7
ACSR | Curlew | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.091 | 75 | 0.1109 | 972.8 | 356 | Southwire | ACSR : 1033.5 : Curlew : 54/7
ACSR | Snowbird | 1033.5 | 42 | 7 | 0.1569 | 0.0872 | 0.2616 | 1.203 |  |  |  | 25 | 0.0925 | 75 | 0.1105 | 973.9 | 141.5 | Southwire | ACSR : 1033.5 : Snowbird : 42/7
ACSR | Ortolan | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0921 | 75 | 0.1101 | 972.8 | 189.9 | Southwire | ACSR : 1033.5 : Ortolan : 45/7
ACSR | Finch | 1113 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.0852 | 75 | 0.1039 | 1053.9 | 376.1 | Southwire | ACSR : 1113 : Finch : 54/19
ACSR | Bluejay | 1113 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.0859 | 75 | 0.1025 | 1048.7 | 204.8 | Southwire | ACSR : 1113 : Bluejay : 45/7
ACSR | Grackle | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.338 |  |  |  | 25 | 0.0798 | 75 | 0.097 | 1128.6 | 402.8 | Southwire | ACSR : 1192.5 : Grackle : 54/19
ACSR | Bunting | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0805 | 75 | 0.0959 | 1123.4 | 219.1 | Southwire | ACSR : 1192.5 : Bunting : 45/7
ACSR | Pheasant | 1272 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0751 | 75 | 0.0914 | 1204.3 | 429.4 | Southwire | ACSR : 1272 : Pheasant : 54/19
ACSR | Bittern | 1272 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0759 | 75 | 0.0902 | 1197.7 | 233.9 | Southwire | ACSR : 1272 : Bittern : 45/7
ACSR | Martin | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.071 | 75 | 0.086 | 1279.1 | 455.9 | Southwire | ACSR : 1351.5 : Martin : 54/19
ACSR | Dipper | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0718 | 75 | 0.0852 | 1272.9 | 248.3 | Southwire | ACSR : 1351.5 : Dipper : 45/7
ACSR | Plover | 1431 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0673 | 75 | 0.0814 | 1354.6 | 483.2 | Southwire | ACSR : 1431 : Plover : 54/19
ACSR | Bobolink | 1431 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0681 | 75 | 0.0808 | 1347.5 | 263.1 | Southwire | ACSR : 1431 : Bobolink : 45/7
ACSR | Parrot | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0641 | 75 | 0.0774 | 1428.8 | 509.2 | Southwire | ACSR : 1510.5 : Parrot : 54/19
ACSR | Nuthatch | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0649 | 75 | 0.0768 | 1422.5 | 277.5 | Southwire | ACSR : 1510.5 : Nuthatch : 45/7
ACSR | Falcon | 1590 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.545 |  |  |  | 25 | 0.0611 | 75 | 0.0737 | 1505 | 537 | Southwire | ACSR : 1590 : Falcon : 54/19
ACSR | Lapwing | 1590 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.062 | 75 | 0.0733 | 1498.1 | 292.2 | Southwire | ACSR : 1590 : Lapwing : 45/7
ACSR | Chukar | 1780 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.0561 | 75 | 0.0658 | 1685.4 | 386.7 | Southwire | ACSR : 1780 : Chukar : 84/19
ACSR | Kiwi | 2167 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0484 | 75 | 0.0562 | 2051.4 | 249.2 | Southwire | ACSR : 2167 : Kiwi : 72/7
ACSR | Bluebird | 2156 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0477 | 75 | 0.0555 | 2040.4 | 467.5 | Southwire | ACSR : 2156 : Bluebird : 84/19
ACSR | Thrasher | 2312 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0457 | 75 | 0.0529 | 2187.9 | 335.4 | Southwire | ACSR : 2312 : Thrasher : 76/19
ACSR | Joree | 2515 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0428 | 75 | 0.0493 | 2380.1 | 364.9 | Southwire | ACSR : 2515 : Joree : 76/19
ACSRAW | Swan/AW | 4 | 6 | 1 | 0.0834 | 0.0834 | 0.0834 | 0.25 | 3.35 |  |  | 25 | 2.1017 | 75 | 2.6801 | 38.9 | 15.6 | Southwire | ACSRAW : 4 : Swan/AW : 6/1
ACSRAW | Swanate/AW | 4 | 7 | 1 | 0.0772 | 0.1029 | 0.1029 | 0.257 | 3.45 |  |  | 25 | 2.0448 | 75 | 2.6555 | 38.9 | 23.8 | Southwire | ACSRAW : 4 : Swanate/AW : 7/1
ACSRAW | Sparrow/AW | 2 | 6 | 1 | 0.1052 | 0.1052 | 0.1052 | 0.316 | 4.23 |  |  | 25 | 1.322 | 75 | 1.7244 | 61.9 | 24.8 | Southwire | ACSRAW : 2 : Sparrow/AW : 6/1
ACSRAW | Sparate/AW | 2 | 7 | 1 | 0.0974 | 0.1299 | 0.1299 | 0.325 | 4.35 |  |  | 25 | 1.286 | 75 | 1.7096 | 61.9 | 37.9 | Southwire | ACSRAW : 2 : Sparate/AW : 7/1
ACSRAW | Robin/AW | 1 | 6 | 1 | 0.1182 | 0.1182 | 0.1182 | 0.355 | 4.75 |  |  | 25 | 1.0483 | 75 | 1.3844 | 78.2 | 31.4 | Southwire | ACSRAW : 1 : Robin/AW : 6/1
ACSRAW | Raven/AW | 1/0 | 6 | 1 | 0.1327 | 0.1327 | 0.1327 | 0.398 | 5.33 |  |  | 25 | 0.8309 | 75 | 1.1119 | 98.5 | 39.5 | Southwire | ACSRAW : 1/0 : Raven/AW : 6/1
ACSRAW | Penguin/AW | 4/0 | 6 | 1 | 0.1878 | 0.1878 | 0.1878 | 0.563 | 7.55 |  |  | 25 | 0.415 | 75 | 0.5855 | 197.4 | 79.1 | Southwire | ACSRAW : 4/0 : Penguin/AW : 6/1
ACSRAW | Waxwing/AW | 266.8 | 18 | 1 | 0.1217 | 0.1217 | 0.1217 | 0.609 |  |  |  | 25 | 0.3433 | 75 | 0.4108 | 249.9 | 33.2 | Southwire | ACSRAW : 266.8 : Waxwing/AW : 18/1
ACSRAW | Partridge/AW | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3328 | 75 | 0.3981 | 251.3 | 97.9 | Southwire | ACSRAW : 266.8 : Partridge/AW : 26/7
ACSRAW | Ostrich/AW | 300 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.2961 | 75 | 0.3542 | 282.5 | 110 | Southwire | ACSRAW : 300 : Ostrich/AW : 26/7
ACSRAW | Merlin/AW | 336.4 | 18 | 1 | 0.1367 | 0.1367 | 0.1367 | 0.684 |  |  |  | 25 | 0.2726 | 75 | 0.3261 | 315.3 | 41.9 | Southwire | ACSRAW : 336.4 : Merlin/AW : 18/1
ACSRAW | Linnet/AW | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.2642 | 75 | 0.316 | 316.6 | 123.3 | Southwire | ACSRAW : 336.4 : Linnet/AW : 26/7
ACSRAW | Oriole/AW | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2588 | 75 | 0.3095 | 317.7 | 176.9 | Southwire | ACSRAW : 336.4 : Oriole/AW : 30/7
ACSRAW | Chickadee/AW | 397.5 | 18 | 1 | 0.1486 | 0.1486 | 0.1486 | 0.743 |  |  |  | 25 | 0.231 | 75 | 0.2762 | 372.6 | 49.6 | Southwire | ACSRAW : 397.5 : Chickadee/AW : 18/1
ACSRAW | Brant/AW | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2263 | 75 | 0.2706 | 374.4 | 116.1 | Southwire | ACSRAW : 397.5 : Brant/AW : 24/7
ACSRAW | Ibis/AW | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2238 | 75 | 0.2676 | 374.1 | 145.7 | Southwire | ACSRAW : 397.5 : Ibis/AW : 26/7
ACSRAW | Lark/AW | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2192 | 75 | 0.2621 | 375.3 | 209 | Southwire | ACSRAW : 397.5 : Lark/AW : 30/7
ACSRAW | Pelican/AW | 477 | 18 | 1 | 0.1628 | 0.1628 | 0.1628 | 0.814 |  |  |  | 25 | 0.1929 | 75 | 0.2305 | 447.2 | 59.5 | Southwire | ACSRAW : 477 : Pelican/AW : 18/1
ACSRAW | Flicker/AW | 477 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1888 | 75 | 0.2257 | 449.4 | 139.4 | Southwire | ACSRAW : 477 : Flicker/AW : 24/7
ACSRAW | Hawk/AW | 477 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1868 | 75 | 0.2232 | 449 | 174.9 | Southwire | ACSRAW : 477 : Hawk/AW : 26/7
ACSRAW | Hen/AW | 477 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.1829 | 75 | 0.2186 | 450.4 | 250.8 | Southwire | ACSRAW : 477 : Hen/AW : 30/7
ACSRAW | Osprey/AW | 556.5 | 18 | 1 | 0.1758 | 0.1758 | 0.1758 | 0.879 |  |  |  | 25 | 0.1657 | 75 | 0.1979 | 521.4 | 69.4 | Southwire | ACSRAW : 556.5 : Osprey/AW : 18/1
ACSRAW | Parakeet/AW | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.1622 | 75 | 0.1937 | 524.3 | 162.5 | Southwire | ACSRAW : 556.5 : Parakeet/AW : 24/7
ACSRAW | Dove/AW | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1603 | 75 | 0.1915 | 524.2 | 204.3 | Southwire | ACSRAW : 556.5 : Dove/AW : 26/7
ACSRAW | Eagle/AW | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.157 | 75 | 0.1875 | 525.5 | 292.6 | Southwire | ACSRAW : 556.5 : Eagle/AW : 30/7
ACSRAW | Peacock/AW | 605 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.1493 | 75 | 0.1783 | 570 | 176.9 | Southwire | ACSRAW : 605 : Peacock/AW : 24/7
ACSRAW | Squab/AW | 605 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1477 | 75 | 0.1763 | 569.5 | 221.9 | Southwire | ACSRAW : 605 : Squab/AW : 26/7
ACSRAW | Kingbird/AW | 636 | 18 | 1 | 0.188 | 0.188 | 0.188 | 0.94 |  |  |  | 25 | 0.1454 | 75 | 0.1735 | 596.3 | 79.3 | Southwire | ACSRAW : 636 : Kingbird/AW : 18/1
ACSRAW | Teal/AW | 605 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1448 | 75 | 0.1729 | 571.2 | 311.4 | Southwire | ACSRAW : 605 : Teal/AW : 30/19
ACSRAW | Rook/AW | 636 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1422 | 75 | 0.1698 | 599.1 | 185.7 | Southwire | ACSRAW : 636 : Rook/AW : 24/7
ACSRAW | Grosbeak/AW | 636 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.99 |  |  |  | 25 | 0.1406 | 75 | 0.1678 | 599 | 233.2 | Southwire | ACSRAW : 636 : Grosbeak/AW : 26/7
ACSRAW | Egret/AW | 636 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1378 | 75 | 0.1646 | 600.5 | 327.7 | Southwire | ACSRAW : 636 : Egret/AW : 30/19
ACSRAW | Flamingo/AW | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1 |  |  |  | 25 | 0.1358 | 75 | 0.1621 | 628.2 | 194.7 | Southwire | ACSRAW : 666.6 : Flamingo/AW : 24/7
ACSRAW | Gannet/AW | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1342 | 75 | 0.1602 | 627.7 | 244.5 | Southwire | ACSRAW : 666.6 : Gannet/AW : 26/7
ACSRAW | Crow/AW | 715.5 | 54 | 7 | 0.1151 | 0.1151 | 0.345 | 1.04 |  |  |  | 25 | 0.1267 | 75 | 0.1552 | 673.8 | 209 | Southwire | ACSRAW : 715.5 : Crow/AW : 54/7
ACSRAW | Starling/AW | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1252 | 75 | 0.1494 | 674 | 262.5 | Southwire | ACSRAW : 715.5 : Starling/AW : 26/7
ACSRAW | Redwing/AW | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1228 | 75 | 0.1465 | 675.3 | 367.9 | Southwire | ACSRAW : 715.5 : Redwing/AW : 30/19
ACSRAW | Tern/AW | 795 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1169 | 75 | 0.1401 | 748.6 | 123.8 | Southwire | ACSRAW : 795 : Tern/AW : 45/7
ACSRAW | Condor/AW | 795 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1143 | 75 | 0.1398 | 748.4 | 232.1 | Southwire | ACSRAW : 795 : Condor/AW : 54/7
ACSRAW | Drake/AW | 795 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.113 | 75 | 0.1347 | 749.1 | 291.7 | Southwire | ACSRAW : 795 : Drake/AW : 26/7
ACSRAW | Mallard/AW | 795 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.1107 | 75 | 0.132 | 750.7 | 409.5 | Southwire | ACSRAW : 795 : Mallard/AW : 30/19
ACSRAW | Ruddy/AW | 900 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1037 | 75 | 0.1243 | 847.4 | 140.3 | Southwire | ACSRAW : 900 : Ruddy/AW : 45/7
ACSRAW | Canary/AW | 900 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1014 | 75 | 0.1238 | 847.7 | 262.9 | Southwire | ACSRAW : 900 : Canary/AW : 54/7
ACSRAW | Rail/AW | 954 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0981 | 75 | 0.1174 | 898.5 | 148.7 | Southwire | ACSRAW : 954 : Rail/AW : 45/7
ACSRAW | Cardinal/AW | 954 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0958 | 75 | 0.1169 | 898.3 | 278.6 | Southwire | ACSRAW : 954 : Cardinal/AW : 54/7
ACSRAW | Ortolan/AW | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0909 | 75 | 0.1087 | 972.8 | 160.9 | Southwire | ACSRAW : 1033.5 : Ortolan/AW : 45/7
ACSRAW | Curlew/AW | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.0888 | 75 | 0.1081 | 972.8 | 301.7 | Southwire | ACSRAW : 1033.5 : Curlew/AW : 54/7
ACSRAW | Finch/AW | 1113 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.0832 | 75 | 0.1012 | 1053.9 | 318.8 | Southwire | ACSRAW : 1113 : Finch/AW : 54/19
ACSRAW | Bluejay/AW | 1113 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.0848 | 75 | 0.1011 | 1048.7 | 173.6 | Southwire | ACSRAW : 1113 : Bluejay/AW : 45/7
ACSRAW | Bunting/AW | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0795 | 75 | 0.0948 | 1123.4 | 185.7 | Southwire | ACSRAW : 1192.5 : Bunting/AW : 45/7
ACSRAW | Grackle/AW | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.333 |  |  |  | 25 | 0.0779 | 75 | 0.0946 | 1128.6 | 341.3 | Southwire | ACSRAW : 1192.5 : Grackle/AW : 54/19
ACSRAW | Bittern/AW | 1272 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0749 | 75 | 0.0891 | 1197.7 | 198.2 | Southwire | ACSRAW : 1272 : Bittern/AW : 45/7
ACSRAW | Pheasant/AW | 1272 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0733 | 75 | 0.0889 | 1204.3 | 363.9 | Southwire | ACSRAW : 1272 : Pheasant/AW : 54/19
ACSRAW | Dipper/AW | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0708 | 75 | 0.0842 | 1272.9 | 210.4 | Southwire | ACSRAW : 1351.5 : Dipper/AW : 45/7
ACSRAW | Martin/AW | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0693 | 75 | 0.0839 | 1279.1 | 386.4 | Southwire | ACSRAW : 1351.5 : Martin/AW : 54/19
ACSRAW | Bobolink/AW | 1431 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0673 | 75 | 0.0798 | 1347.5 | 223 | Southwire | ACSRAW : 1431 : Bobolink/AW : 45/7
ACSRAW | Plover/AW | 1431 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0658 | 75 | 0.0795 | 1354.6 | 409.5 | Southwire | ACSRAW : 1431 : Plover/AW : 54/19
ACSRAW | Nuthatch/AW | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0641 | 75 | 0.0759 | 1422.5 | 235.2 | Southwire | ACSRAW : 1510.5 : Nuthatch/AW : 45/7
ACSRAW | Parrot/AW | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0626 | 75 | 0.0756 | 1428.8 | 431.6 | Southwire | ACSRAW : 1510.5 : Parrot/AW : 54/19
ACSRAW | Lapwing/AW | 1590 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0612 | 75 | 0.0724 | 1498.1 | 247.6 | Southwire | ACSRAW : 1590 : Lapwing/AW : 45/7
ACSRAW | Falcon/AW | 1590 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.545 |  |  |  | 25 | 0.0597 | 75 | 0.072 | 1505 | 455.1 | Southwire | ACSRAW : 1590 : Falcon/AW : 54/19
ACSRAW | Chukar/AW | 1780 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.0553 | 75 | 0.0649 | 1685.4 | 327.7 | Southwire | ACSRAW : 1780 : Chukar/AW : 84/19
ACSRAW | Kiwi/AW | 2167 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0481 | 75 | 0.0558 | 2051.4 | 211.2 | Southwire | ACSRAW : 2167 : Kiwi/AW : 72/7
ACSRAW | Bluebird/AW | 2156 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0471 | 75 | 0.0548 | 2040.4 | 396.2 | Southwire | ACSRAW : 2156 : Bluebird/AW : 84/19
ACSRAW | Thrasher/AW | 2312 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0453 | 75 | 0.0524 | 2187.9 | 284.2 | Southwire | ACSRAW : 2312 : Thrasher/AW : 76/19
ACSRAW | Joree/AW | 2515 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0424 | 75 | 0.0489 | 2380.1 | 309.2 | Southwire | ACSRAW : 2515 : Joree/AW : 76/19
ACSRTW | Merlin/TW | 336.4 | 14 | 1 |  | 0.1367 | 0.1367 | 0.63 |  | 6 | 2 | 25 | 0.2756 | 75 | 0.3298 | 315.5 | 49.5 | Southwire | ACSRTW : 336.4 : Merlin/TW : 14/1
ACSRTW | Monongahela/TW | 405.1 | 14 | 1 |  | 0.152 | 0.152 | 0.68 |  | 6 | 2 | 25 | 0.2291 | 75 | 0.274 | 379.8 | 61.2 | Southwire | ACSRTW : 405.1 : Monongahela/TW : 14/1
ACSRTW | Flicker/TW | 477 | 18 | 7 |  | 0.094 | 0.282 | 0.776 |  | 13 | 2 | 25 | 0.193 | 75 | 0.2307 | 448.4 | 164.4 | Southwire | ACSRTW : 477 : Flicker/TW : 18/7
ACSRTW | Hawk/TW | 477 | 18 | 7 |  | 0.1053 | 0.3159 | 0.789 |  | 16 | 2 | 25 | 0.1923 | 75 | 0.2298 | 448.7 | 206.3 | Southwire | ACSRTW : 477 : Hawk/TW : 18/7
ACSRTW | Parakeet/TW | 556.5 | 18 | 7 |  | 0.1015 | 0.3045 | 0.835 |  | 13 | 2 | 25 | 0.1657 | 75 | 0.198 | 523.2 | 191.7 | Southwire | ACSRTW : 556.5 : Parakeet/TW : 18/7
ACSRTW | Dove/TW | 556.5 | 20 | 7 |  | 0.1138 | 0.3414 | 0.852 |  | 16 | 2 | 25 | 0.165 | 75 | 0.1972 | 523.5 | 241 | Southwire | ACSRTW : 556.5 : Dove/TW : 20/7
ACSRTW | Calumet/TW | 565.3 | 20 | 7 |  | 0.1146 | 0.3441 | 0.858 |  | 16 | 2 | 25 | 0.1625 | 75 | 0.1941 | 531 | 244.8 | Southwire | ACSRTW : 565.3 : Calumet/TW : 20/7
ACSRTW | Mohawk/TW | 571.7 | 18 | 7 |  | 0.103 | 0.309 | 0.846 |  | 13 | 2 | 25 | 0.1613 | 75 | 0.1928 | 537.3 | 197.4 | Southwire | ACSRTW : 571.7 : Mohawk/TW : 18/7
ACSRTW | Swift/TW | 636 | 27 | 1 |  | 0.1329 | 0.1329 | 0.85 |  | 3 | 3 | 25 | 0.1482 | 75 | 0.1816 | 599.2 | 46.8 | Southwire | ACSRTW : 636 : Swift/TW : 27/1
ACSRTW | Rook/TW | 636 | 18 | 7 |  | 0.1085 | 0.3255 | 0.89 |  | 13 | 2 | 25 | 0.1452 | 75 | 0.1735 | 597.9 | 219.1 | Southwire | ACSRTW : 636 : Rook/TW : 18/7
ACSRTW | Grosbeak/TW | 636 | 20 | 7 |  | 0.1216 | 0.3648 | 0.908 |  | 16 | 2 | 25 | 0.1446 | 75 | 0.1727 | 598.4 | 275.1 | Southwire | ACSRTW : 636 : Grosbeak/TW : 20/7
ACSRTW | Mystic/TW | 666.6 | 20 | 7 |  | 0.1111 | 0.3333 | 0.913 |  | 13 | 2 | 25 | 0.1387 | 75 | 0.1656 | 626.6 | 229.7 | Southwire | ACSRTW : 666.6 : Mystic/TW : 20/7
ACSRTW | Oswego/TW | 664.8 | 20 | 7 |  | 0.1244 | 0.3732 | 0.927 |  | 16 | 2 | 25 | 0.1385 | 75 | 0.1653 | 625.4 | 288 | Southwire | ACSRTW : 664.8 : Oswego/TW : 20/7
ACSRTW | Nechako/TW | 768.9 | 27 | 1 |  | 0.152 | 0.152 | 0.93 |  | 3 | 3 | 25 | 0.1232 | 75 | 0.1506 | 720.7 | 61.2 | Southwire | ACSRTW : 768.9 : Nechako/TW : 27/1
ACSRTW | Wabash/TW | 762.8 | 20 | 7 |  | 0.1331 | 0.3343 | 0.99 |  | 16 | 2 | 25 | 0.1212 | 75 | 0.1446 | 717 | 330 | Southwire | ACSRTW : 762.8 : Wabash/TW : 20/7
ACSRTW | Maumee/TW | 768.2 | 20 | 7 |  | 0.1195 | 0.3585 | 0.977 |  | 13 | 2 | 25 | 0.1207 | 75 | 0.1439 | 722.1 | 265.7 | Southwire | ACSRTW : 768.2 : Maumee/TW : 20/7
ACSRTW | Tern/TW | 795 | 17 | 7 |  | 0.0886 | 0.2658 | 0.96 |  | 7 | 2 | 25 | 0.1178 | 75 | 0.1405 | 745.9 | 146.1 | Southwire | ACSRTW : 795 : Tern/TW : 17/7
ACSRTW | Puffin/TW | 795 | 18 | 7 |  | 0.1108 | 0.3324 | 0.98 |  | 10 | 2 | 25 | 0.1171 | 75 | 0.1396 | 746.9 | 228.4 | Southwire | ACSRTW : 795 : Puffin/TW : 18/7
ACSRTW | Condor/TW | 795 | 20 | 7 |  | 0.1213 | 0.3639 | 0.993 |  | 13 | 2 | 25 | 0.1167 | 75 | 0.1392 | 747.2 | 273.8 | Southwire | ACSRTW : 795 : Condor/TW : 20/7
ACSRTW | Drake/TW | 795 | 20 | 7 |  | 0.136 | 0.408 | 1.01 |  | 16 | 2 | 25 | 0.1161 | 75 | 0.1386 | 747.8 | 344.2 | Southwire | ACSRTW : 795 : Drake/TW : 20/7
ACSRTW | Fraser/TW | 946.7 | 35 | 7 |  | 0.1154 | 0.3462 | 1.077 |  | 10 | 3 | 25 | 0.0995 | 75 | 0.1214 | 894 | 248 | Southwire | ACSRTW : 946.7 : Fraser/TW : 35/7
ACSRTW | Phoenix/TW | 954 | 30 | 7 |  | 0.0837 | 0.2511 | 1.044 |  | 5 | 3 | 25 | 0.0996 | 75 | 0.1213 | 901.6 | 130.4 | Southwire | ACSRTW : 954 : Phoenix/TW : 30/7
ACSRTW | Rail/TW | 954 | 32 | 7 |  | 0.0971 | 0.2913 | 1.061 |  | 7 | 3 | 25 | 0.0993 | 75 | 0.121 | 900 | 175 | Southwire | ACSRTW : 954 : Rail/TW : 32/7
ACSRTW | Kettle/TW | 957.2 | 32 | 7 |  | 0.0973 | 0.2919 | 1.06 |  | 7 | 3 | 25 | 0.099 | 75 | 0.1206 | 902.8 | 176.2 | Southwire | ACSRTW : 957.2 : Kettle/TW : 32/7
ACSRTW | Cardinal/TW | 954 | 20 | 7 |  | 0.1329 | 0.3987 | 1.084 |  | 13 | 2 | 25 | 0.0977 | 75 | 0.1164 | 897.3 | 328.7 | Southwire | ACSRTW : 954 : Cardinal/TW : 20/7
ACSRTW | Suwannee/TW | 959.6 | 22 | 7 |  | 0.1493 | 0.4479 | 1.108 |  | 16 | 2 | 25 | 0.0967 | 75 | 0.1152 | 903 | 415 | Southwire | ACSRTW : 959.6 : Suwannee/TW : 22/7
ACSRTW | Columbia/TW | 966.2 | 21 | 7 |  | 0.1338 | 0.4014 | 1.092 |  | 13 | 2 | 25 | 0.0966 | 75 | 0.115 | 908 | 333 | Southwire | ACSRTW : 966.2 : Columbia/TW : 21/7
ACSRTW | Snowbird/TW | 1033.5 | 30 | 7 |  | 0.0871 | 0.2613 | 1.089 |  | 5 | 3 | 25 | 0.0923 | 75 | 0.1123 | 973.8 | 141.2 | Southwire | ACSRTW : 1033.5 : Snowbird/TW : 30/7
ACSRTW | Ortolan/TW | 1033.5 | 32 | 7 |  | 0.101 | 0.303 | 1.102 |  | 7 | 3 | 25 | 0.092 | 75 | 0.112 | 975.2 | 189.8 | Southwire | ACSRTW : 1033.5 : Ortolan/TW : 32/7
ACSRTW | Curlew/TW | 1033.5 | 21 | 7 |  | 0.1363 | 0.4149 | 1.129 |  | 13 | 2 | 25 | 0.0905 | 75 | 0.1077 | 971.1 | 355.9 | Southwire | ACSRTW : 1033.5 : Curlew/TW : 21/7
ACSRTW | Avocet/TW | 1113 | 30 | 7 |  | 0.0904 | 0.2712 | 1.129 |  | 5 | 3 | 25 | 0.0861 | 75 | 0.1045 | 1048.9 | 152.1 | Southwire | ACSRTW : 1113 : Avocet/TW : 30/7
ACSRTW | Bluejay/TW | 1113 | 33 | 7 |  | 0.1049 | 0.3147 | 1.143 |  | 7 | 3 | 25 | 0.0858 | 75 | 0.1042 | 1052.2 | 204.8 | Southwire | ACSRTW : 1113 : Bluejay/TW : 33/7
ACSRTW | Finch/TW | 1113 | 38 | 19 |  | 0.0862 | 0.431 | 1.185 |  | 13 | 3 | 25 | 0.0848 | 75 | 0.1032 | 1052.6 | 376.4 | Southwire | ACSRTW : 1113 : Finch/TW : 38/19
ACSRTW | Genesee/TW | 1158 | 33 | 7 |  | 0.1078 | 0.3234 | 1.165 |  | 7 | 3 | 25 | 0.0826 | 75 | 0.1003 | 1092 | 216 | Southwire | ACSRTW : 1158 : Genesee/TW : 33/7
ACSRTW | Cheyenne/TW | 1168.1 | 30 | 7 |  | 0.0926 | 0.2778 | 1.155 |  | 5 | 3 | 25 | 0.0823 | 75 | 0.0998 | 1100.4 | 159.6 | Southwire | ACSRTW : 1168.1 : Cheyenne/TW : 30/7
ACSRTW | Oxbird/TW | 1192.5 | 30 | 7 |  | 0.0936 | 0.2808 | 1.167 |  | 5 | 3 | 25 | 0.0807 | 75 | 0.0978 | 1123 | 163 | Southwire | ACSRTW : 1192.5 : Oxbird/TW : 30/7
ACSRTW | Bunting/TW | 1192.5 | 33 | 7 |  | 0.1085 | 0.3255 | 1.181 |  | 7 | 3 | 25 | 0.0804 | 75 | 0.0975 | 1124 | 219 | Southwire | ACSRTW : 1192.5 : Bunting/TW : 33/7
ACSRTW | Grackle/TW | 1192.5 | 38 | 19 |  | 0.0892 | 0.446 | 1.225 |  | 13 | 3 | 25 | 0.0794 | 75 | 0.0965 | 1127 | 403 | Southwire | ACSRTW : 1192.5 : Grackle/TW : 38/19
ACSRTW | Hudson/TW | 1158.4 | 26 | 7 |  | 0.1467 | 0.4401 | 1.196 |  | 13 | 2 | 25 | 0.0811 | 75 | 0.0964 | 1089 | 400 | Southwire | ACSRTW : 1158.4 : Hudson/TW : 26/7
ACSRTW | Yukon/TW | 1233.6 | 38 | 19 |  | 0.091 | 0.455 | 1.245 |  | 13 | 3 | 25 | 0.0769 | 75 | 0.0934 | 1166.5 | 419.5 | Southwire | ACSRTW : 1233.6 : Yukon/TW : 38/19
ACSRTW | Nelson/TW | 1257.1 | 35 | 7 |  | 0.1115 | 0.3345 | 1.213 |  | 7 | 3 | 25 | 0.0765 | 75 | 0.0927 | 1185.7 | 231.3 | Southwire | ACSRTW : 1257.1 : Nelson/TW : 35/7
ACSRTW | Catawba/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.076 | 75 | 0.092 | 1198 | 174 | Southwire | ACSRTW : 1272 : Catawba/TW : 30/7
ACSRTW | Scissortail/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.076 | 75 | 0.092 | 1198 | 174 | Southwire | ACSRTW : 1272 : Scissortail/TW : 30/7
ACSRTW | Bittern/TW | 1272 | 35 | 7 |  | 0.1121 | 0.3363 | 1.22 |  | 7 | 3 | 25 | 0.0757 | 75 | 0.0917 | 1199 | 234 | Southwire | ACSRTW : 1272 : Bittern/TW : 35/7
ACSRTW | Pheasant/TW | 1272 | 39 | 19 |  | 0.0921 | 0.4605 | 1.264 |  | 13 | 3 | 25 | 0.0747 | 75 | 0.0907 | 1202 | 430 | Southwire | ACSRTW : 1272 : Pheasant/TW : 39/19
ACSRTW | Thames/TW | 1334.6 | 39 | 19 |  | 0.0944 | 0.472 | 1.29 |  | 13 | 3 | 25 | 0.0714 | 75 | 0.0866 | 1261.6 | 451.4 | Southwire | ACSRTW : 1334.6 : Thames/TW : 39/19
ACSRTW | Dipper/TW | 1351.5 | 35 | 7 |  | 0.1155 | 0.3465 | 1.256 |  | 7 | 3 | 25 | 0.0716 | 75 | 0.0865 | 1274 | 248 | Southwire | ACSRTW : 1351.5 : Dipper/TW : 35/7
ACSRTW | Mackenzie/TW | 1359.7 | 36 | 7 |  | 0.1159 | 0.3477 | 1.259 |  | 7 | 3 | 25 | 0.0712 | 75 | 0.086 | 1280 | 250 | Southwire | ACSRTW : 1359.7 : Mackenzie/TW : 36/7
ACSRTW | Truckee/TW | 1372.5 | 30 | 7 |  | 0.1004 | 0.3012 | 1.248 |  | 5 | 3 | 25 | 0.0709 | 75 | 0.0856 | 1293.4 | 187.6 | Southwire | ACSRTW : 1372.5 : Truckee/TW : 30/7
ACSRTW | Martin/TW | 1351.5 | 39 | 19 |  | 0.0949 | 0.4745 | 1.3 |  | 13 | 3 | 25 | 0.0706 | 75 | 0.0856 | 1278 | 456 | Southwire | ACSRTW : 1351.5 : Martin/TW : 39/19
ACSRTW | Bobolink/TW | 1431 | 36 | 7 |  | 0.1189 | 0.3567 | 1.291 |  | 7 | 3 | 25 | 0.0679 | 75 | 0.082 | 1350 | 263 | Southwire | ACSRTW : 1431 : Bobolink/TW : 36/7
ACSRTW | Plover/TW | 1431 | 39 | 19 |  | 0.0977 | 0.4885 | 1.337 |  | 13 | 3 | 25 | 0.0669 | 75 | 0.081 | 1353 | 483 | Southwire | ACSRTW : 1431 : Plover/TW : 39/19
ACSRTW | Merrimack/TW | 1433.6 | 39 | 19 |  | 0.0978 | 0.489 | 1.34 |  | 13 | 3 | 25 | 0.0668 | 75 | 0.0809 | 1356 | 434 | Southwire | ACSRTW : 1433.6 : Merrimack/TW : 39/19
ACSRTW | Miramichi/TW | 1455.3 | 36 | 7 |  | 0.12 | 0.36 | 1.302 |  | 7 | 3 | 25 | 0.0669 | 75 | 0.0807 | 1372 | 268 | Southwire | ACSRTW : 1455.3 : Miramichi/TW : 36/7
ACSRTW | St. Croix/TW | 1467.8 | 33 | 7 |  | 0.1041 | 0.3123 | 1.292 |  | 5 | 3 | 25 | 0.0667 | 75 | 0.0804 | 1383 | 202 | Southwire | ACSRTW : 1467.8 : St. Croix/TW : 33/7
ACSRTW | Rio Grande/TW | 1533.3 | 39 | 19 |  | 0.1012 | 0.506 | 1.382 |  | 13 | 3 | 25 | 0.0628 | 75 | 0.0758 | 1449 | 519 | Southwire | ACSRTW : 1533.3 : Rio Grande/TW : 39/19
ACSRTW | Potomac/TW | 1557.4 | 36 | 7 |  | 0.1241 | 0.3723 | 1.345 |  | 7 | 3 | 25 | 0.0629 | 75 | 0.0757 | 1468 | 287 | Southwire | ACSRTW : 1557.4 : Potomac/TW : 36/7
ACSRTW | Platte/TW | 1569 | 33 | 7 |  | 0.1074 | 0.3222 | 1.334 |  | 5 | 3 | 25 | 0.0629 | 75 | 0.0756 | 1478 | 215 | Southwire | ACSRTW : 1569 : Platte/TW : 33/7
ACSRTW | Lapwing/TW | 1590 | 36 | 7 |  | 0.1253 | 0.3759 | 1.358 |  | 7 | 3 | 25 | 0.0618 | 75 | 0.0743 | 1499 | 292 | Southwire | ACSRTW : 1590 : Lapwing/TW : 36/7
ACSRTW | Falcon/TW | 1590 | 42 | 19 |  | 0.103 | 0.515 | 1.408 |  | 13 | 3 | 25 | 0.0607 | 75 | 0.0733 | 1503 | 537 | Southwire | ACSRTW : 1590 : Falcon/TW : 42/19
ACSRTW | Pecos/TW | 1622 | 39 | 19 |  | 0.1064 | 0.532 | 1.424 |  | 13 | 3 | 25 | 0.0595 | 75 | 0.0718 | 1533 | 574 | Southwire | ACSRTW : 1622 : Pecos/TW : 39/19
ACSRTW | Schuylkill/TW | 1657.4 | 36 | 7 |  | 0.128 | 0.384 | 1.386 |  | 7 | 3 | 25 | 0.0595 | 75 | 0.0715 | 1563 | 305 | Southwire | ACSRTW : 1657.4 : Schuylkill/TW : 36/7
ACSRTW | Pee Dee/TW | 1758.6 | 37 | 7 |  | 0.1319 | 0.3957 | 1.427 |  | 7 | 3 | 25 | 0.0565 | 75 | 0.0677 | 1658 | 324 | Southwire | ACSRTW : 1758.6 : Pee Dee/TW : 37/7
ACSRTW | James/TW | 1730.6 | 39 | 19 |  | 0.1075 | 0.5375 | 1.47 |  | 13 | 3 | 25 | 0.0562 | 75 | 0.0677 | 1636 | 585 | Southwire | ACSRTW : 1730.6 : James/TW : 39/19
ACSRTW | Chukar/TW | 1780 | 37 | 19 |  | 0.0874 | 0.437 | 1.445 |  | 8 | 3 | 25 | 0.0555 | 75 | 0.0666 | 1676 | 387 | Southwire | ACSRTW : 1780 : Chukar/TW : 37/19
ACSRTW | Cumberland/TW | 1926.9 | 42 | 19 |  | 0.1133 | 0.5665 | 1.545 |  | 13 | 3 | 25 | 0.0511 | 75 | 0.0613 | 1821 | 650 | Southwire | ACSRTW : 1926.9 : Cumberland/TW : 42/19
ACSRTW | Athabaska/TW | 1949.6 | 42 | 7 |  | 0.1392 | 0.4176 | 1.504 |  | 7 | 3 | 25 | 0.0517 | 75 | 0.0607 | 1838 | 361 | Southwire | ACSRTW : 1949.6 : Athabaska/TW : 42/7
ACSRTW | Powder/TW | 2153.8 | 64 | 19 |  | 0.0961 | 0.4805 | 1.602 |  | 8 | 4 | 25 | 0.0475 | 75 | 0.0554 | 2030 | 468 | Southwire | ACSRTW : 2153.8 : Powder/TW : 64/19
ACSRTW | Bluebird/TW | 2156 | 64 | 19 |  | 0.0961 | 0.4805 | 1.608 |  | 8 | 4 | 25 | 0.0475 | 75 | 0.0554 | 2047 | 468 | Southwire | ACSRTW : 2156 : Bluebird/TW : 64/19
ACSRTW | Santee/TW | 2627.3 | 64 | 19 |  | 0.1062 | 0.531 | 1.762 |  | 8 | 4 | 25 | 0.0405 | 75 | 0.0468 | 2477 | 571 | Southwire | ACSRTW : 2627.3 : Santee/TW : 64/19
ACSS | Partridge/ACSS | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.3343 | 75 | 0.4019 | 251.3 | 115.6 | Southwire | ACSS : 266.8 : Partridge/ACSS : 26/7
ACSS | Junco/ACSS | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.66 |  |  |  | 25 | 0.332 | 75 | 0.3991 | 251.3 | 165.5 | Southwire | ACSS : 266.8 : Junco/ACSS : 30/7
ACSS | Ostrich/ACSS | 300 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.2974 | 75 | 0.3575 | 282.5 | 129.8 | Southwire | ACSS : 300 : Ostrich/ACSS : 26/7
ACSS | WoodCock/ACSS | 336.4 | 22 | 7 | 0.1237 | 0.0687 | 0.2061 | 0.701 |  |  |  | 25 | 0.2677 | 75 | 0.3218 | 317.1 | 87.8 | Southwire | ACSS : 336.4 : WoodCock/ACSS : 22/7
ACSS | Linnet/ACSS | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.2654 | 75 | 0.319 | 316.6 | 145.5 | Southwire | ACSS : 336.4 : Linnet/ACSS : 26/7
ACSS | Oriole/ACSS | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2635 | 75 | 0.3167 | 317.7 | 208.7 | Southwire | ACSS : 336.4 : Oriole/ACSS : 30/7
ACSS | Ptarmigan/ACSS | 397.5 | 20 | 7 | 0.141 | 0.0627 | 0.1881 | 0.752 |  |  |  | 25 | 0.2277 | 75 | 0.2737 | 374.5 | 73.2 | Southwire | ACSS : 397.5 : Ptarmigan/ACSS : 20/7
ACSS | Brant/ACSS | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2258 | 75 | 0.2714 | 374.4 | 137 | Southwire | ACSS : 397.5 : Brant/ACSS : 24/7
ACSS | Ibis/ACSS | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2248 | 75 | 0.2701 | 374.1 | 171.9 | Southwire | ACSS : 397.5 : Ibis/ACSS : 26/7
ACSS | Lark/ACSS | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2232 | 75 | 0.2681 | 375.3 | 246.6 | Southwire | ACSS : 397.5 : Lark/ACSS : 30/7
ACSS | Tailorbird/ACSS | 477 | 20 | 7 | 0.1544 | 0.0686 | 0.2058 | 0.824 |  |  |  | 25 | 0.1901 | 75 | 0.2284 | 449.1 | 87.6 | Southwire | ACSS : 477 : Tailorbird/ACSS : 20/7
ACSS | Flicker/ACSS | 477 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1885 | 75 | 0.2264 | 449.4 | 164.5 | Southwire | ACSS : 477 : Flicker/ACSS : 24/7
ACSS | Hawk/ACSS | 477 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1876 | 75 | 0.2253 | 449 | 206.4 | Southwire | ACSS : 477 : Hawk/ACSS : 26/7
ACSS | Hen/ACSS | 477 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.1862 | 75 | 0.2236 | 450.4 | 296 | Southwire | ACSS : 477 : Hen/ACSS : 30/7
ACSS | Sapsucker/ACSS | 556.5 | 22 | 7 | 0.159 | 0.0883 | 0.2649 | 0.901 |  |  |  | 25 | 0.1626 | 75 | 0.1952 | 523.9 | 145.1 | Southwire | ACSS : 556.5 : Sapsucker/ACSS : 22/7
ACSS | Parakeet/ACSS | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.1618 | 75 | 0.1943 | 524.3 | 191.8 | Southwire | ACSS : 556.5 : Parakeet/ACSS : 24/7
ACSS | Dove/ACSS | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.161 | 75 | 0.1933 | 524.2 | 241 | Southwire | ACSS : 556.5 : Dove/ACSS : 26/7
ACSS | Peacock/ACSS | 605 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.149 | 75 | 0.1789 | 570 | 208.7 | Southwire | ACSS : 605 : Peacock/ACSS : 24/7
ACSS | Squab/ACSS | 605 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1483 | 75 | 0.178 | 569.5 | 261.8 | Southwire | ACSS : 605 : Squab/ACSS : 26/7
ACSS | Teal/ACSS | 605 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1472 | 75 | 0.1767 | 571.2 | 367.5 | Southwire | ACSS : 605 : Teal/ACSS : 30/19
ACSS | Wood Duck/ACSS | 605 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1471 | 75 | 0.1766 | 571.2 | 375.3 | Southwire | ACSS : 605 : Wood Duck/ACSS : 30/7
ACSS | Goldfinch/ACSS | 636 | 22 | 7 | 0.17 | 0.0944 | 0.2832 | 0.963 |  |  |  | 25 | 0.1426 | 75 | 0.1711 | 598.9 | 165.9 | Southwire | ACSS : 636 : Goldfinch/ACSS : 22/7
ACSS | Rook/ACSS | 636 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1419 | 75 | 0.1702 | 599.1 | 219.1 | Southwire | ACSS : 636 : Rook/ACSS : 24/7
ACSS | Grosbeak/ACSS | 636 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.991 |  |  |  | 25 | 0.1412 | 75 | 0.1694 | 599 | 275.2 | Southwire | ACSS : 636 : Grosbeak/ACSS : 26/7
ACSS | Egret/ACSS | 636 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1402 | 75 | 0.1682 | 600.5 | 386.7 | Southwire | ACSS : 636 : Egret/ACSS : 30/19
ACSS | Scoter/ACSS | 636 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1401 | 75 | 0.1681 | 600.5 | 394.6 | Southwire | ACSS : 636 : Scoter/ACSS : 30/7
ACSS | Flamingo/ACSS | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1 |  |  |  | 25 | 0.1355 | 75 | 0.1625 | 628.2 | 229.7 | Southwire | ACSS : 666.6 : Flamingo/ACSS : 24/7
ACSS | Gannet/ACSS | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1348 | 75 | 0.1617 | 627.7 | 288.5 | Southwire | ACSS : 666.6 : Gannet/ACSS : 26/7
ACSS | Stilt/ACSS | 715.5 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.036 |  |  |  | 25 | 0.1264 | 75 | 0.1516 | 674.2 | 246.6 | Southwire | ACSS : 715.5 : Stilt/ACSS : 24/7
ACSS | Starling/ACSS | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.1258 | 75 | 0.1508 | 674 | 309.7 | Southwire | ACSS : 715.5 : Starling/ACSS : 26/7
ACSS | Redwing/ACSS | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1248 | 75 | 0.1497 | 675.3 | 434.1 | Southwire | ACSS : 715.5 : Redwing/ACSS : 30/19
ACSS | Condor/ACSS | 795 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1141 | 75 | 0.1406 | 748.4 | 273.9 | Southwire | ACSS : 795 : Condor/ACSS : 54/7
ACSS | Tern/ACSS | 795 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1153 | 75 | 0.139 | 748.6 | 146.1 | Southwire | ACSS : 795 : Tern/ACSS : 45/7
ACSS | Macaw/ACSS | 795 | 42 | 7 | 0.1376 | 0.0764 | 0.2292 | 1.055 |  |  |  | 25 | 0.1157 | 75 | 0.1385 | 749 | 108.6 | Southwire | ACSS : 795 : Macaw/ACSS : 42/7
ACSS | Puffin/ACSS | 795 | 22 | 7 | 0.1901 | 0.1056 | 0.3168 | 1.077 |  |  |  | 25 | 0.1147 | 75 | 0.1374 | 748.8 | 207.6 | Southwire | ACSS : 795 : Puffin/ACSS : 22/7
ACSS | Cuckoo/ACSS | 795 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1141 | 75 | 0.1367 | 748.8 | 273.9 | Southwire | ACSS : 795 : Cuckoo/ACSS : 24/7
ACSS | Drake/ACSS | 795 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.1135 | 75 | 0.1359 | 749.1 | 344.3 | Southwire | ACSS : 795 : Drake/ACSS : 26/7
ACSS | Mallard/ACSS | 795 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.1125 | 75 | 0.1349 | 750.7 | 483.2 | Southwire | ACSS : 795 : Mallard/ACSS : 30/19
ACSS | Canary/ACSS | 900 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.1012 | 75 | 0.1245 | 847.7 | 310.2 | Southwire | ACSS : 900 : Canary/ACSS : 54/7
ACSS | Ruddy/ACSS | 900 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.1023 | 75 | 0.1232 | 847.4 | 165.5 | Southwire | ACSS : 900 : Ruddy/ACSS : 45/7
ACSS | Cardinal/ACSS | 954 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0956 | 75 | 0.1176 | 898.3 | 328.7 | Southwire | ACSS : 954 : Cardinal/ACSS : 54/7
ACSS | Rail/ACSS | 954 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0968 | 75 | 0.1164 | 898.5 | 175.5 | Southwire | ACSS : 954 : Rail/ACSS : 45/7
ACSS | Corncrake/ACSS | 954 | 20 | 7 | 0.2184 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0968 | 75 | 0.1156 | 898.5 | 175.5 | Southwire | ACSS : 954 : Corncrake/ACSS : 20/7
ACSS | Towhee/ACSS | 954 | 48 | 7 | 0.141 | 0.1097 | 0.3291 | 1.175 |  |  |  | 25 | 0.0964 | 75 | 0.1152 | 898.8 | 224 | Southwire | ACSS : 954 : Towhee/ACSS : 48/7
ACSS | Redbird/ACSS | 954 | 24 | 7 | 0.1994 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0956 | 75 | 0.1144 | 898.8 | 328.7 | Southwire | ACSS : 954 : Redbird/ACSS : 24/7
ACSS | Canvasback/ACSS | 954 | 30 | 19 | 0.1783 | 0.107 | 0.535 | 1.248 |  |  |  | 25 | 0.0942 | 75 | 0.1128 | 900.5 | 579.6 | Southwire | ACSS : 954 : Canvasback/ACSS : 30/19
ACSS | Curlew/ACSS | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.0886 | 75 | 0.1087 | 972.8 | 356 | Southwire | ACSS : 1033.5 : Curlew/ACSS : 54/7
ACSS | Ortolan/ACSS | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0897 | 75 | 0.1077 | 972.8 | 189.9 | Southwire | ACSS : 1033.5 : Ortolan/ACSS : 45/7
ACSS | Snowbird/ACSS | 1033.5 | 42 | 7 | 0.1569 | 0.0872 | 0.2616 | 1.203 |  |  |  | 25 | 0.0901 | 75 | 0.1074 | 973.9 | 141.5 | Southwire | ACSS : 1033.5 : Snowbird/ACSS : 42/7
ACSS | Finch/ACSS | 1113 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.292 |  |  |  | 25 | 0.083 | 75 | 0.1017 | 1053.9 | 376.1 | Southwire | ACSS : 1113 : Finch/ACSS : 54/19
ACSS | Bluejay/ACSS | 1113 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.258 |  |  |  | 25 | 0.0837 | 75 | 0.1003 | 1048.7 | 204.8 | Southwire | ACSS : 1113 : Bluejay/ACSS : 45/7
ACSS | Grackle/ACSS | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.337 |  |  |  | 25 | 0.0777 | 75 | 0.0951 | 1128.6 | 402.8 | Southwire | ACSS : 1192.5 : Grackle/ACSS : 54/19
ACSS | Bunting/ACSS | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0785 | 75 | 0.0939 | 1123.4 | 219.1 | Southwire | ACSS : 1192.5 : Bunting/ACSS : 45/7
ACSS | Pheasant/ACSS | 1272 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.381 |  |  |  | 25 | 0.0732 | 75 | 0.0894 | 1204.3 | 429.4 | Southwire | ACSS : 1272 : Pheasant/ACSS : 54/19
ACSS | Bittern/ACSS | 1272 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.0739 | 75 | 0.0884 | 1197.7 | 233.9 | Southwire | ACSS : 1272 : Bittern/ACSS : 45/7
ACSS | Martin/ACSS | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0692 | 75 | 0.0844 | 1279.1 | 455.9 | Southwire | ACSS : 1351.5 : Martin/ACSS : 54/19
ACSS | Dipper/ACSS | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0699 | 75 | 0.0835 | 1272.9 | 248.3 | Southwire | ACSS : 1351.5 : Dipper/ACSS : 45/7
ACSS | Plover/ACSS | 1431 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0656 | 75 | 0.0799 | 1354.6 | 483.2 | Southwire | ACSS : 1431 : Plover/ACSS : 54/19
ACSS | Bobolink/ACSS | 1431 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0664 | 75 | 0.0791 | 1347.5 | 263.1 | Southwire | ACSS : 1431 : Bobolink/ACSS : 45/7
ACSS | Parrot/ACSS | 1510.5 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0624 | 75 | 0.0759 | 1428.8 | 509.2 | Southwire | ACSS : 1510.5 : Parrot/ACSS : 54/19
ACSS | Nuthatch/ACSS | 1510.5 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0633 | 75 | 0.0752 | 1422.5 | 277.5 | Southwire | ACSS : 1510.5 : Nuthatch/ACSS : 45/7
ACSS | Falcon/ACSS | 1590 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.544 |  |  |  | 25 | 0.0596 | 75 | 0.0724 | 1505 | 537 | Southwire | ACSS : 1590 : Falcon/ACSS : 54/19
ACSS | Ratite/ACSS | 1590 | 42 | 7 | 0.1946 | 0.1081 | 0.3243 | 1.492 |  |  |  | 25 | 0.0608 | 75 | 0.0718 | 1498.1 | 217.5 | Southwire | ACSS : 1590 : Ratite/ACSS : 42/7
ACSS | Lapwing/ACSS | 1590 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0605 | 75 | 0.0718 | 1498.1 | 292.2 | Southwire | ACSS : 1590 : Lapwing/ACSS : 45/7
ACSS | Chukar/ACSS | 1780 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.601 |  |  |  | 25 | 0.0547 | 75 | 0.0645 | 1685.4 | 386.7 | Southwire | ACSS : 1780 : Chukar/ACSS : 84/19
ACSS | Mockingbird/ACSS | 2034.5 | 72 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.681 |  |  |  | 25 | 0.0498 | 75 | 0.0581 | 1925.7 | 233.9 | Southwire | ACSS : 2034.5 : Mockingbird/ACSS : 72/7
ACSS | Roadrunner/ACSS | 2057 | 76 | 19 | 0.1645 | 0.0768 | 0.384 | 1.7 |  |  |  | 25 | 0.049 | 75 | 0.0573 | 1946.5 | 298.6 | Southwire | ACSS : 2057 : Roadrunner/ACSS : 76/19
ACSS | Kiwi/ACSS | 2167 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.0473 | 75 | 0.0551 | 2051.4 | 249.2 | Southwire | ACSS : 2167 : Kiwi/ACSS : 72/7
ACSS | Bluebird/ACSS | 2156 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.0466 | 75 | 0.0544 | 2040.4 | 467.5 | Southwire | ACSS : 2156 : Bluebird/ACSS : 84/19
ACSS | Thrasher/ACSS | 2312 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0447 | 75 | 0.0519 | 2187.9 | 335.4 | Southwire | ACSS : 2312 : Thrasher/ACSS : 76/19
ACSS | Joree/ACSS | 2515 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0419 | 75 | 0.0484 | 2380.1 | 364.9 | Southwire | ACSS : 2515 : Joree/ACSS : 76/19
ACSSAW | Partridge/ACSS/AW | 266.8 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.642 |  |  |  | 25 | 0.324 | 75 | 0.3894 | 251.3 | 97.9 | Southwire | ACSSAW : 266.8 : Partridge/ACSS/AW : 26/7
ACSSAW | Junco/ACSS/AW | 266.8 | 30 | 7 | 0.0943 | 0.0943 | 0.2829 | 0.66 |  |  |  | 25 | 0.3176 | 75 | 0.3816 | 251.3 | 140.2 | Southwire | ACSSAW : 266.8 : Junco/ACSS/AW : 30/7
ACSSAW | Ostrich/ACSS/AW | 300 | 26 | 7 | 0.1074 | 0.0835 | 0.2505 | 0.68 |  |  |  | 25 | 0.2883 | 75 | 0.3464 | 282.5 | 110 | Southwire | ACSSAW : 300 : Ostrich/ACSS/AW : 26/7
ACSSAW | WoodCock/ACSS/AW | 336.4 | 22 | 7 | 0.1237 | 0.0687 | 0.2061 | 0.701 |  |  |  | 25 | 0.2626 | 75 | 0.3156 | 317.1 | 74.4 | Southwire | ACSSAW : 336.4 : WoodCock/ACSS/AW : 22/7
ACSSAW | Linnet/ACSS/AW | 336.4 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 0.72 |  |  |  | 25 | 0.2572 | 75 | 0.309 | 316.6 | 123.2 | Southwire | ACSSAW : 336.4 : Linnet/ACSS/AW : 26/7
ACSSAW | Oriole/ACSS/AW | 336.4 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 0.741 |  |  |  | 25 | 0.2521 | 75 | 0.3028 | 317.7 | 176.9 | Southwire | ACSSAW : 336.4 : Oriole/ACSS/AW : 30/7
ACSSAW | Ptarmigan/ACSS/AW | 397.5 | 20 | 7 | 0.141 | 0.0627 | 0.1881 | 0.752 |  |  |  | 25 | 0.2247 | 75 | 0.27 | 374.5 | 62 | Southwire | ACSSAW : 397.5 : Ptarmigan/ACSS/AW : 20/7
ACSSAW | Brant/ACSS/AW | 397.5 | 24 | 7 | 0.1287 | 0.0858 | 0.2574 | 0.772 |  |  |  | 25 | 0.2202 | 75 | 0.2646 | 374.4 | 116.1 | Southwire | ACSSAW : 397.5 : Brant/ACSS/AW : 24/7
ACSSAW | Ibis/ACSS/AW | 397.5 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 0.783 |  |  |  | 25 | 0.2179 | 75 | 0.2617 | 374.1 | 145.6 | Southwire | ACSSAW : 397.5 : Ibis/ACSS/AW : 26/7
ACSSAW | Lark/ACSS/AW | 397.5 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 0.806 |  |  |  | 25 | 0.2135 | 75 | 0.2564 | 375.3 | 208.9 | Southwire | ACSSAW : 397.5 : Lark/ACSS/AW : 30/7
ACSSAW | Tailorbird/ACSS/AW | 477 | 20 | 7 | 0.1544 | 0.0686 | 0.2058 | 0.823 |  |  |  | 25 | 0.1876 | 75 | 0.2253 | 449.1 | 74.2 | Southwire | ACSSAW : 477 : Tailorbird/ACSS/AW : 20/7
ACSSAW | Flicker/ACSS/AW | 477 | 24 | 7 | 0.141 | 0.094 | 0.282 | 0.846 |  |  |  | 25 | 0.1838 | 75 | 0.2207 | 449.4 | 139.4 | Southwire | ACSSAW : 477 : Flicker/ACSS/AW : 24/7
ACSSAW | Hawk/ACSS/AW | 477 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 0.858 |  |  |  | 25 | 0.1818 | 75 | 0.2183 | 449 | 174.9 | Southwire | ACSSAW : 477 : Hawk/ACSS/AW : 26/7
ACSSAW | Hen/ACSS/AW | 477 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 0.883 |  |  |  | 25 | 0.1782 | 75 | 0.2139 | 450.4 | 250.8 | Southwire | ACSSAW : 477 : Hen/ACSS/AW : 30/7
ACSSAW | Sapsucker/ACSS/AW | 556.5 | 22 | 7 | 0.159 | 0.0883 | 0.2649 | 0.901 |  |  |  | 25 | 0.1596 | 75 | 0.1915 | 523.9 | 123 | Southwire | ACSSAW : 556.5 : Sapsucker/ACSS/AW : 22/7
ACSSAW | Parakeet/ACSS/AW | 556.5 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 0.914 |  |  |  | 25 | 0.1579 | 75 | 0.1894 | 524.3 | 162.5 | Southwire | ACSSAW : 556.5 : Parakeet/ACSS/AW : 24/7
ACSSAW | Dove/ACSS/AW | 556.5 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 0.927 |  |  |  | 25 | 0.1561 | 75 | 0.1873 | 524.2 | 204.2 | Southwire | ACSSAW : 556.5 : Dove/ACSS/AW : 26/7
ACSSAW | Eagle/ACSS/AW | 556.5 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 0.953 |  |  |  | 25 | 0.153 | 75 | 0.1835 | 525.5 | 292.6 | Southwire | ACSSAW : 556.5 : Eagle/ACSS/AW : 30/7
ACSSAW | Peacock/ACSS/AW | 605 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 0.953 |  |  |  | 25 | 0.1454 | 75 | 0.1744 | 570 | 176.9 | Southwire | ACSSAW : 605 : Peacock/ACSS/AW : 24/7
ACSSAW | Squab/ACSS/AW | 605 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 0.966 |  |  |  | 25 | 0.1438 | 75 | 0.1725 | 569.5 | 221.8 | Southwire | ACSSAW : 605 : Squab/ACSS/AW : 26/7
ACSSAW | Teal/ACSS/AW | 605 | 30 | 19 | 0.142 | 0.0852 | 0.426 | 0.994 |  |  |  | 25 | 0.1411 | 75 | 0.1692 | 571.2 | 311.4 | Southwire | ACSSAW : 605 : Teal/ACSS/AW : 30/19
ACSSAW | Wood Duck/ACSS/AW | 605 | 30 | 7 | 0.142 | 0.142 | 0.426 | 0.994 |  |  |  | 25 | 0.1408 | 75 | 0.1689 | 571.2 | 318 | Southwire | ACSSAW : 605 : Wood Duck/ACSS/AW : 30/7
ACSSAW | Goldfinch/ACSS/AW | 636 | 22 | 7 | 0.17 | 0.0944 | 0.2832 | 0.963 |  |  |  | 25 | 0.14 | 75 | 0.1678 | 598.9 | 140.5 | Southwire | ACSSAW : 636 : Goldfinch/ACSS/AW : 22/7
ACSSAW | Rook/ACSS/AW | 636 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 0.977 |  |  |  | 25 | 0.1384 | 75 | 0.166 | 599.1 | 185.7 | Southwire | ACSSAW : 636 : Rook/ACSS/AW : 24/7
ACSSAW | Grosbeak/ACSS/AW | 636 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 0.99 |  |  |  | 25 | 0.1369 | 75 | 0.1642 | 599 | 233.2 | Southwire | ACSSAW : 636 : Grosbeak/ACSS/AW : 26/7
ACSSAW | Egret/ACSS/AW | 636 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.019 |  |  |  | 25 | 0.1343 | 75 | 0.161 | 600.5 | 327.6 | Southwire | ACSSAW : 636 : Egret/ACSS/AW : 30/19
ACSSAW | Scoter/ACSS/AW | 636 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.019 |  |  |  | 25 | 0.1341 | 75 | 0.1608 | 600.5 | 334.3 | Southwire | ACSSAW : 636 : Scoter/ACSS/AW : 30/7
ACSSAW | Flamingo/ACSS/AW | 666.6 | 24 | 7 | 0.1667 | 0.1111 | 0.3333 | 1 |  |  |  | 25 | 0.1322 | 75 | 0.1585 | 628.2 | 194.7 | Southwire | ACSSAW : 666.6 : Flamingo/ACSS/AW : 24/7
ACSSAW | Gannet/ACSS/AW | 666.6 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.014 |  |  |  | 25 | 0.1307 | 75 | 0.1567 | 627.7 | 244.5 | Southwire | ACSSAW : 666.6 : Gannet/ACSS/AW : 26/7
ACSSAW | Stilt/ACSS/AW | 715.5 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.036 |  |  |  | 25 | 0.1234 | 75 | 0.1478 | 674.2 | 208.9 | Southwire | ACSSAW : 715.5 : Stilt/ACSS/AW : 24/7
ACSSAW | Starling/ACSS/AW | 715.5 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.051 |  |  |  | 25 | 0.122 | 75 | 0.1462 | 674 | 262.4 | Southwire | ACSSAW : 715.5 : Starling/ACSS/AW : 26/7
ACSSAW | Redwing/ACSS/AW | 715.5 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.081 |  |  |  | 25 | 0.1196 | 75 | 0.1434 | 675.3 | 367.8 | Southwire | ACSSAW : 715.5 : Redwing/ACSS/AW : 30/19
ACSSAW | Tern/ACSS/AW | 795 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.063 |  |  |  | 25 | 0.1138 | 75 | 0.1372 | 748.6 | 123.8 | Southwire | ACSSAW : 795 : Tern/ACSS/AW : 45/7
ACSSAW | Condor/ACSS/AW | 795 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1113 | 75 | 0.1372 | 748.4 | 232.1 | Southwire | ACSSAW : 795 : Condor/ACSS/AW : 54/7
ACSSAW | Macaw/ACSS/AW | 795 | 42 | 7 | 0.1376 | 0.0764 | 0.2292 | 1.055 |  |  |  | 25 | 0.1146 | 75 | 0.1371 | 749 | 92.1 | Southwire | ACSSAW : 795 : Macaw/ACSS/AW : 42/7
ACSSAW | Cuckoo/ACSS/AW | 795 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.092 |  |  |  | 25 | 0.1113 | 75 | 0.1333 | 748.8 | 232.1 | Southwire | ACSSAW : 795 : Cuckoo/ACSS/AW : 24/7
ACSSAW | Drake/ACSS/AW | 795 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.108 |  |  |  | 25 | 0.11 | 75 | 0.1318 | 749.1 | 291.7 | Southwire | ACSSAW : 795 : Drake/ACSS/AW : 26/7
ACSSAW | Mallard/ACSS/AW | 795 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.14 |  |  |  | 25 | 0.1079 | 75 | 0.1292 | 750.7 | 409.4 | Southwire | ACSSAW : 795 : Mallard/ACSS/AW : 30/19
ACSSAW | Ruddy/ACSS/AW | 900 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.131 |  |  |  | 25 | 0.101 | 75 | 0.1216 | 847.4 | 140.2 | Southwire | ACSSAW : 900 : Ruddy/ACSS/AW : 45/7
ACSSAW | Canary/ACSS/AW | 900 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.162 |  |  |  | 25 | 0.0987 | 75 | 0.1214 | 847.7 | 262.9 | Southwire | ACSSAW : 900 : Canary/ACSS/AW : 54/7
ACSSAW | Rail/ACSS/AW | 954 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0956 | 75 | 0.1149 | 898.5 | 148.7 | Southwire | ACSSAW : 954 : Rail/ACSS/AW : 45/7
ACSSAW | Cardinal/ACSS/AW | 954 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0934 | 75 | 0.1147 | 898.3 | 278.6 | Southwire | ACSSAW : 954 : Cardinal/ACSS/AW : 54/7
ACSSAW | Corncrake/ACSS/AW | 954 | 20 | 7 | 0.2184 | 0.0971 | 0.2913 | 1.165 |  |  |  | 25 | 0.0956 | 75 | 0.1141 | 898.5 | 148.7 | Southwire | ACSSAW : 954 : Corncrake/ACSS/AW : 20/7
ACSSAW | Towhee/ACSS/AW | 954 | 48 | 7 | 0.141 | 0.1097 | 0.3291 | 1.175 |  |  |  | 25 | 0.0948 | 75 | 0.1132 | 898.8 | 189.8 | Southwire | ACSSAW : 954 : Towhee/ACSS/AW : 48/7
ACSSAW | Redbird/ACSS/AW | 954 | 24 | 7 | 0.1994 | 0.1329 | 0.3987 | 1.196 |  |  |  | 25 | 0.0934 | 75 | 0.1116 | 898.8 | 278.6 | Southwire | ACSSAW : 954 : Redbird/ACSS/AW : 24/7
ACSSAW | Canvasback/ACSS/AW | 954 | 30 | 19 | 0.1783 | 0.107 | 0.535 | 1.248 |  |  |  | 25 | 0.0903 | 75 | 0.108 | 900.5 | 491.1 | Southwire | ACSSAW : 954 : Canvasback/ACSS/AW : 30/19
ACSSAW | Snowbird/ACSS/AW | 1033.5 | 42 | 7 | 0.1569 | 0.0872 | 0.2616 | 1.203 |  |  |  | 25 | 0.0892 | 75 | 0.1064 | 973.9 | 119.9 | Southwire | ACSSAW : 1033.5 : Snowbird/ACSS/AW : 42/7
ACSSAW | Ortolan/ACSS/AW | 1033.5 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.212 |  |  |  | 25 | 0.0886 | 75 | 0.1063 | 972.8 | 160.9 | Southwire | ACSSAW : 1033.5 : Ortolan/ACSS/AW : 45/7
ACSSAW | Curlew/ACSS/AW | 1033.5 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.245 |  |  |  | 25 | 0.0865 | 75 | 0.1061 | 972.8 | 301.7 | Southwire | ACSSAW : 1033.5 : Curlew/ACSS/AW : 54/7
ACSSAW | Finch/ACSS/AW | 1113 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.293 |  |  |  | 25 | 0.081 | 75 | 0.0993 | 1053.9 | 318.7 | Southwire | ACSSAW : 1113 : Finch/ACSS/AW : 54/19
ACSSAW | Bluejay/ACSS/AW | 1113 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.259 |  |  |  | 25 | 0.0826 | 75 | 0.099 | 1048.7 | 173.5 | Southwire | ACSSAW : 1113 : Bluejay/ACSS/AW : 45/7
ACSSAW | Grackle/ACSS/AW | 1192.5 | 54 | 19 | 0.1486 | 0.0892 | 0.446 | 1.338 |  |  |  | 25 | 0.076 | 75 | 0.0929 | 1128.6 | 341.3 | Southwire | ACSSAW : 1192.5 : Grackle/ACSS/AW : 54/19
ACSSAW | Bunting/ACSS/AW | 1192.5 | 45 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.302 |  |  |  | 25 | 0.0775 | 75 | 0.0927 | 1123.4 | 185.7 | Southwire | ACSSAW : 1192.5 : Bunting/ACSS/AW : 45/7
ACSSAW | Pheasant/ACSS/AW | 1272 | 54 | 19 | 0.1535 | 0.0921 | 0.4605 | 1.382 |  |  |  | 25 | 0.0715 | 75 | 0.0873 | 1204.3 | 363.8 | Southwire | ACSSAW : 1272 : Pheasant/ACSS/AW : 54/19
ACSSAW | Bittern/ACSS/AW | 1272 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.345 |  |  |  | 25 | 0.073 | 75 | 0.0872 | 1197.7 | 198.2 | Southwire | ACSSAW : 1272 : Bittern/ACSS/AW : 45/7
ACSSAW | Dipper/ACSS/AW | 1351.5 | 45 | 7 | 0.1733 | 0.1155 | 0.3465 | 1.386 |  |  |  | 25 | 0.0691 | 75 | 0.0824 | 1272.9 | 210.4 | Southwire | ACSSAW : 1351.5 : Dipper/ACSS/AW : 45/7
ACSSAW | Martin/ACSS/AW | 1351.5 | 54 | 19 | 0.1582 | 0.0949 | 0.4745 | 1.424 |  |  |  | 25 | 0.0676 | 75 | 0.0824 | 1279.1 | 386.3 | Southwire | ACSSAW : 1351.5 : Martin/ACSS/AW : 54/19
ACSSAW | Bobolink/ACSS/AW | 1431 | 45 | 7 | 0.1783 | 0.1189 | 0.3567 | 1.427 |  |  |  | 25 | 0.0656 | 75 | 0.0781 | 1347.5 | 223 | Southwire | ACSSAW : 1431 : Bobolink/ACSS/AW : 45/7
ACSSAW | Plover/ACSS/AW | 1431 | 54 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.465 |  |  |  | 25 | 0.0641 | 75 | 0.0781 | 1354.6 | 409.4 | Southwire | ACSSAW : 1431 : Plover/ACSS/AW : 54/19
ACSSAW | Nuthatch/ACSS/AW | 1510 | 45 | 7 | 0.1832 | 0.1221 | 0.3663 | 1.466 |  |  |  | 25 | 0.0625 | 75 | 0.0743 | 1422.5 | 235.1 | Southwire | ACSSAW : 1510 : Nuthatch/ACSS/AW : 45/7
ACSSAW | Parrot/ACSS/AW | 1510 | 54 | 19 | 0.1672 | 0.1003 | 0.5015 | 1.505 |  |  |  | 25 | 0.0611 | 75 | 0.0742 | 1428.8 | 431.5 | Southwire | ACSSAW : 1510 : Parrot/ACSS/AW : 54/19
ACSSAW | Ratite/ACSS/AW | 1590 | 42 | 7 | 0.1946 | 0.1081 | 0.3243 | 1.492 |  |  |  | 25 | 0.0603 | 75 | 0.0711 | 1498.1 | 184.3 | Southwire | ACSSAW : 1590 : Ratite/ACSS/AW : 42/7
ACSSAW | Lapwing/ACSS/AW | 1590 | 45 | 7 | 0.188 | 0.1253 | 0.3759 | 1.504 |  |  |  | 25 | 0.0597 | 75 | 0.0709 | 1498.1 | 247.6 | Southwire | ACSSAW : 1590 : Lapwing/ACSS/AW : 45/7
ACSSAW | Falcon/ACSS/AW | 1590 | 54 | 19 | 0.1716 | 0.103 | 0.515 | 1.544 |  |  |  | 25 | 0.0583 | 75 | 0.0707 | 1505 | 455 | Southwire | ACSSAW : 1590 : Falcon/ACSS/AW : 54/19
ACSSAW | Chukar/ACSS/AW | 1780 | 84 | 19 | 0.1456 | 0.0874 | 0.437 | 1.602 |  |  |  | 25 | 0.054 | 75 | 0.0635 | 1685.4 | 327.6 | Southwire | ACSSAW : 1780 : Chukar/ACSS/AW : 84/19
ACSSAW | Mockingbird/ACSS/AW | 2034.5 | 72 | 7 | 0.1681 | 0.1121 | 0.3363 | 1.681 |  |  |  | 25 | 0.0494 | 75 | 0.0577 | 1925.7 | 198.2 | Southwire | ACSSAW : 2034.5 : Mockingbird/ACSS/AW : 72/7
ACSSAW | Roadrunner/ACSS/AW | 2057 | 76 | 19 | 0.1645 | 0.0768 | 0.384 | 1.7 |  |  |  | 25 | 0.0486 | 75 | 0.0568 | 1946.5 | 253 | Southwire | ACSSAW : 2057 : Roadrunner/ACSS/AW : 76/19
ACSSAW | Kiwi/ACSS/AW | 2167 | 72 | 7 | 0.1735 | 0.1157 | 0.3471 | 1.735 |  |  |  | 25 | 0.047 | 75 | 0.0547 | 2051.4 | 211.1 | Southwire | ACSSAW : 2167 : Kiwi/ACSS/AW : 72/7
ACSSAW | Bluebird/ACSS/AW | 2156 | 84 | 19 | 0.1602 | 0.0961 | 0.4805 | 1.762 |  |  |  | 25 | 0.046 | 75 | 0.0537 | 2040.4 | 396.1 | Southwire | ACSSAW : 2156 : Bluebird/ACSS/AW : 84/19
ACSSAW | Thrasher/ACSS/AW | 2312 | 76 | 19 | 0.1744 | 0.0814 | 0.407 | 1.802 |  |  |  | 25 | 0.0443 | 75 | 0.0514 | 2187.9 | 284.2 | Southwire | ACSSAW : 2312 : Thrasher/ACSS/AW : 76/19
ACSSAW | Joree/ACSS/AW | 2515 | 76 | 19 | 0.1819 | 0.0849 | 0.4245 | 1.88 |  |  |  | 25 | 0.0415 | 75 | 0.048 | 2380.1 | 309.2 | Southwire | ACSSAW : 2515 : Joree/ACSS/AW : 76/19
ACSSAWTW | Linnet/ACSS/AW/TW | 336.4 | 18 | 7 |  | 0.0884 | 0.2652 | 0.659 |  | 16 | 2 | 25 | 0.2566 | 75 | 0.3083 | 315.9 | 123.2 | Southwire | ACSSAWTW : 336.4 : Linnet/ACSS/AW/TW : 18/7
ACSSAWTW | Oriole/ACSS/AW/TW | 336.4 | 16 | 7 |  | 0.1059 | 0.3177 | 0.693 |  | 23 | 2 | 25 | 0.2509 | 75 | 0.3014 | 316.1 | 176.9 | Southwire | ACSSAWTW : 336.4 : Oriole/ACSS/AW/TW : 16/7
ACSSAWTW | Flicker/ACSS/AW/TW | 477 | 18 | 7 |  | 0.094 | 0.282 | 0.776 |  | 13 | 2 | 25 | 0.1831 | 75 | 0.2199 | 447.8 | 139.4 | Southwire | ACSSAWTW : 477 : Flicker/ACSS/AW/TW : 18/7
ACSSAWTW | Hawk/ACSS/AW/TW | 477 | 18 | 7 |  | 0.1053 | 0.3159 | 0.789 |  | 16 | 2 | 25 | 0.1813 | 75 | 0.2177 | 448.1 | 174.9 | Southwire | ACSSAWTW : 477 : Hawk/ACSS/AW/TW : 18/7
ACSSAWTW | Hen/ACSS/AW/TW | 477 | 16 | 7 |  | 0.1261 | 0.3783 | 0.825 |  | 23 | 2 | 25 | 0.1773 | 75 | 0.2128 | 448.3 | 250.8 | Southwire | ACSSAWTW : 477 : Hen/ACSS/AW/TW : 16/7
ACSSAWTW | Parakeet/ACSS/AW/TW | 556.5 | 18 | 7 |  | 0.1015 | 0.3045 | 0.835 |  | 13 | 2 | 25 | 0.1573 | 75 | 0.1887 | 522.4 | 162.5 | Southwire | ACSSAWTW : 556.5 : Parakeet/ACSS/AW/TW : 18/7
ACSSAWTW | Dove/ACSS/AW/TW | 556.5 | 20 | 7 |  | 0.1138 | 0.3414 | 0.852 |  | 16 | 2 | 25 | 0.1557 | 75 | 0.1868 | 522.9 | 204.2 | Southwire | ACSSAWTW : 556.5 : Dove/ACSS/AW/TW : 20/7
ACSSAWTW | Calumet/ACSS/AW/TW | 565.3 | 20 | 7 |  | 0.1146 | 0.3441 | 0.858 |  | 16 | 2 | 25 | 0.1533 | 75 | 0.1839 | 531.2 | 207.5 | Southwire | ACSSAWTW : 565.3 : Calumet/ACSS/AW/TW : 20/7
ACSSAWTW | Mohawk/ACSS/AW/TW | 571.7 | 18 | 7 |  | 0.103 | 0.309 | 0.846 |  | 13 | 2 | 25 | 0.1531 | 75 | 0.1837 | 536.6 | 167.3 | Southwire | ACSSAWTW : 571.7 : Mohawk/ACSS/AW/TW : 18/7
ACSSAWTW | Rook/ACSS/AW/TW | 636 | 18 | 7 |  | 0.1085 | 0.3255 | 0.89 |  | 13 | 2 | 25 | 0.1379 | 75 | 0.1654 | 597 | 185.7 | Southwire | ACSSAWTW : 636 : Rook/ACSS/AW/TW : 18/7
ACSSAWTW | Grosbeak/ACSS/AW/TW | 636 | 20 | 7 |  | 0.1216 | 0.3648 | 0.908 |  | 16 | 2 | 25 | 0.1365 | 75 | 0.1637 | 597.6 | 233.2 | Southwire | ACSSAWTW : 636 : Grosbeak/ACSS/AW/TW : 20/7
ACSSAWTW | Scoter/ACSS/AW/TW | 636 | 18 | 7 |  | 0.1456 | 0.4368 | 0.953 |  | 23 | 2 | 25 | 0.1334 | 75 | 0.1599 | 597.6 | 334.3 | Southwire | ACSSAWTW : 636 : Scoter/ACSS/AW/TW : 18/7
ACSSAWTW | Mystic/ACSS/AW/TW | 666.6 | 20 | 7 |  | 0.1111 | 0.3333 | 0.913 |  | 13 | 2 | 25 | 0.1317 | 75 | 0.1579 | 625.7 | 194.7 | Southwire | ACSSAWTW : 666.6 : Mystic/ACSS/AW/TW : 20/7
ACSSAWTW | Oswego/ACSS/AW/TW | 664.8 | 20 | 7 |  | 0.1244 | 0.3732 | 0.927 |  | 16 | 2 | 25 | 0.1306 | 75 | 0.1567 | 624.6 | 244.1 | Southwire | ACSSAWTW : 664.8 : Oswego/ACSS/AW/TW : 20/7
ACSSAWTW | Maumee/ACSS/AW/TW | 768.2 | 20 | 7 |  | 0.1195 | 0.3585 | 0.977 |  | 13 | 2 | 25 | 0.1146 | 75 | 0.1373 | 721.1 | 225.2 | Southwire | ACSSAWTW : 768.2 : Maumee/ACSS/AW/TW : 20/7
ACSSAWTW | Wabash/ACSS/AW/TW | 762.8 | 20 | 7 |  | 0.1331 | 0.3993 | 0.99 |  | 16 | 2 | 25 | 0.1142 | 75 | 0.1368 | 716.7 | 279.4 | Southwire | ACSSAWTW : 762.8 : Wabash/ACSS/AW/TW : 20/7
ACSSAWTW | Tern/ACSS/AW/TW | 795 | 17 | 7 |  | 0.0886 | 0.2658 | 0.96 |  | 7 | 2 | 25 | 0.1132 | 75 | 0.1355 | 745.2 | 123.8 | Southwire | ACSSAWTW : 795 : Tern/ACSS/AW/TW : 17/7
ACSSAWTW | Puffin/ACSS/AW/TW | 795 | 18 | 7 |  | 0.1108 | 0.3324 | 0.98 |  | 10 | 2 | 25 | 0.1116 | 75 | 0.1337 | 745.9 | 193.6 | Southwire | ACSSAWTW : 795 : Puffin/ACSS/AW/TW : 18/7
ACSSAWTW | Condor/ACSS/AW/TW | 795 | 20 | 7 |  | 0.1213 | 0.3639 | 0.993 |  | 13 | 2 | 25 | 0.1108 | 75 | 0.1327 | 746.3 | 232.1 | Southwire | ACSSAWTW : 795 : Condor/ACSS/AW/TW : 20/7
ACSSAWTW | Drake/ACSS/AW/TW | 795 | 20 | 7 |  | 0.136 | 0.408 | 1.01 |  | 16 | 2 | 25 | 0.1096 | 75 | 0.1313 | 747 | 291.7 | Southwire | ACSSAWTW : 795 : Drake/ACSS/AW/TW : 20/7
ACSSAWTW | Canary/ACSS/AW/TW | 900 | 20 | 7 |  | 0.1291 | 0.3873 | 1.055 |  | 13 | 3 | 25 | 0.0989 | 75 | 0.1212 | 845.6 | 262.9 | Southwire | ACSSAWTW : 900 : Canary/ACSS/AW/TW : 20/7
ACSSAWTW | Phoenix/ACSS/AW/TW | 954 | 30 | 7 |  | 0.0837 | 0.2511 | 1.044 |  | 5 | 3 | 25 | 0.0961 | 75 | 0.1175 | 897.7 | 110.5 | Southwire | ACSSAWTW : 954 : Phoenix/ACSS/AW/TW : 30/7
ACSSAWTW | Rail/ACSS/AW/TW | 954 | 32 | 7 |  | 0.0971 | 0.2913 | 1.061 |  | 7 | 3 | 25 | 0.0955 | 75 | 0.1168 | 898.6 | 148.7 | Southwire | ACSSAWTW : 954 : Rail/ACSS/AW/TW : 32/7
ACSSAWTW | Fraser/ACSS/AW/TW | 946.7 | 35 | 7 |  | 0.1154 | 0.3462 | 1.077 |  | 10 | 3 | 25 | 0.0951 | 75 | 0.1165 | 892.6 | 210 | Southwire | ACSSAWTW : 946.7 : Fraser/ACSS/AW/TW : 35/7
ACSSAWTW | Kettle/ACSS/AW/TW | 957.2 | 32 | 7 |  | 0.0973 | 0.2919 | 1.06 |  | 7 | 3 | 25 | 0.0952 | 75 | 0.1164 | 901.6 | 149.3 | Southwire | ACSSAWTW : 957.2 : Kettle/ACSS/AW/TW : 32/7
ACSSAWTW | Cardinal/ACSS/AW/TW | 954 | 20 | 7 |  | 0.1329 | 0.3987 | 1.084 |  | 13 | 2 | 25 | 0.0929 | 75 | 0.1111 | 895.5 | 278.6 | Southwire | ACSSAWTW : 954 : Cardinal/ACSS/AW/TW : 20/7
ACSSAWTW | Columbia/ACSS/AW/TW | 966.2 | 21 | 7 |  | 0.1338 | 0.4014 | 1.092 |  | 13 | 2 | 25 | 0.0917 | 75 | 0.1097 | 906.9 | 282.3 | Southwire | ACSSAWTW : 966.2 : Columbia/ACSS/AW/TW : 21/7
ACSSAWTW | Suwannee/ACSS/AW/TW | 959.6 | 22 | 7 |  | 0.1493 | 0.4479 | 1.108 |  | 16 | 2 | 25 | 0.0913 | 75 | 0.1092 | 901.6 | 351.5 | Southwire | ACSSAWTW : 959.6 : Suwannee/ACSS/AW/TW : 22/7
ACSSAWTW | Snowbird/ACSS/AW/TW | 1033.5 | 30 | 7 |  | 0.0871 | 0.2613 | 1.089 |  | 5 | 3 | 25 | 0.0891 | 75 | 0.1087 | 972.5 | 119.6 | Southwire | ACSSAWTW : 1033.5 : Snowbird/ACSS/AW/TW : 30/7
ACSSAWTW | Ortolan/ACSS/AW/TW | 1033.5 | 32 | 7 |  | 0.101 | 0.303 | 1.102 |  | 7 | 3 | 25 | 0.0885 | 75 | 0.1081 | 973.4 | 160.9 | Southwire | ACSSAWTW : 1033.5 : Ortolan/ACSS/AW/TW : 32/7
ACSSAWTW | Curlew/ACSS/AW/TW | 1033.5 | 20 | 7 |  | 0.1383 | 0.4149 | 1.129 |  | 13 | 2 | 25 | 0.086 | 75 | 0.1027 | 970.1 | 301.7 | Southwire | ACSSAWTW : 1033.5 : Curlew/ACSS/AW/TW : 20/7
ACSSAWTW | Avocet/ACSS/AW/TW | 1113 | 30 | 7 |  | 0.0904 | 0.2712 | 1.129 |  | 5 | 3 | 25 | 0.0831 | 75 | 0.1012 | 1047.3 | 128.9 | Southwire | ACSSAWTW : 1113 : Avocet/ACSS/AW/TW : 30/7
ACSSAWTW | Bluejay/ACSS/AW/TW | 1113 | 33 | 7 |  | 0.1049 | 0.3147 | 1.143 |  | 7 | 3 | 25 | 0.0825 | 75 | 0.1006 | 1048.3 | 173.5 | Southwire | ACSSAWTW : 1113 : Bluejay/ACSS/AW/TW : 33/7
ACSSAWTW | Finch/ACSS/AW/TW | 1113 | 38 | 19 |  | 0.0862 | 0.431 | 1.185 |  | 13 | 3 | 25 | 0.0807 | 75 | 0.0986 | 1051 | 318.7 | Southwire | ACSSAWTW : 1113 : Finch/ACSS/AW/TW : 38/19
ACSSAWTW | Genesee/ACSS/AW/TW | 1158 | 33 | 7 |  | 0.1078 | 0.3234 | 1.165 |  | 7 | 3 | 25 | 0.0795 | 75 | 0.0968 | 1091 | 183.3 | Southwire | ACSSAWTW : 1158 : Genesee/ACSS/AW/TW : 33/7
ACSSAWTW | Cheyenne/ACSS/AW/TW | 1168.1 | 30 | 7 |  | 0.0926 | 0.2778 | 1.155 |  | 5 | 3 | 25 | 0.0794 | 75 | 0.0967 | 1099 | 135.2 | Southwire | ACSSAWTW : 1168.1 : Cheyenne/ACSS/AW/TW : 30/7
ACSSAWTW | Oxbird/ACSS/AW/TW | 1192.5 | 30 | 7 |  | 0.0936 | 0.2808 | 1.167 |  | 5 | 3 | 25 | 0.0779 | 75 | 0.0948 | 1122 | 138.2 | Southwire | ACSSAWTW : 1192.5 : Oxbird/ACSS/AW/TW : 30/7
ACSSAWTW | Bunting/ACSS/AW/TW | 1192.5 | 33 | 7 |  | 0.1085 | 0.3255 | 1.181 |  | 7 | 3 | 25 | 0.0773 | 75 | 0.0941 | 1123.2 | 185.7 | Southwire | ACSSAWTW : 1192.5 : Bunting/ACSS/AW/TW : 33/7
ACSSAWTW | Grackle/ACSS/AW/TW | 1192.5 | 38 | 19 |  | 0.0892 | 0.446 | 1.225 |  | 13 | 3 | 25 | 0.0756 | 75 | 0.0922 | 1126 | 341.3 | Southwire | ACSSAWTW : 1192.5 : Grackle/ACSS/AW/TW : 38/19
ACSSAWTW | Hudson/ACSS/AW/TW | 1158.4 | 25 | 7 |  | 0.1467 | 0.4401 | 1.196 |  | 13 | 2 | 25 | 0.0772 | 75 | 0.092 | 1087.4 | 339.4 | Southwire | ACSSAWTW : 1158.4 : Hudson/ACSS/AW/TW : 25/7
ACSSAWTW | Nelson/ACSS/AW/TW | 1257.1 | 35 | 7 |  | 0.1115 | 0.3345 | 1.213 |  | 7 | 3 | 25 | 0.0736 | 75 | 0.0895 | 1184 | 196.1 | Southwire | ACSSAWTW : 1257.1 : Nelson/ACSS/AW/TW : 35/7
ACSSAWTW | Yukon/ACSS/AW/TW | 1233.6 | 38 | 19 |  | 0.091 | 0.455 | 1.245 |  | 13 | 3 | 25 | 0.0732 | 75 | 0.0892 | 1166.5 | 355.2 | Southwire | ACSSAWTW : 1233.6 : Yukon/ACSS/AW/TW : 38/19
ACSSAWTW | Catawba/ACSS/AW/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0734 | 75 | 0.0891 | 1196.9 | 147.5 | Southwire | ACSSAWTW : 1272 : Catawba/ACSS/AW/TW : 30/7
ACSSAWTW | Scissortail/ACSS/AW/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0734 | 75 | 0.0891 | 1198 | 147.5 | Southwire | ACSSAWTW : 1272 : Scissortail/ACSS/AW/TW : 30/7
ACSSAWTW | Bittern/ACSS/AW/TW | 1272 | 35 | 7 |  | 0.1121 | 0.3363 | 1.22 |  | 7 | 3 | 25 | 0.0729 | 75 | 0.0885 | 1198.1 | 198.2 | Southwire | ACSSAWTW : 1272 : Bittern/ACSS/AW/TW : 35/7
ACSSAWTW | Pheasant/ACSS/AW/TW | 1272 | 39 | 19 |  | 0.0921 | 0.4605 | 1.264 |  | 13 | 3 | 25 | 0.0712 | 75 | 0.0866 | 1201 | 363.8 | Southwire | ACSSAWTW : 1272 : Pheasant/ACSS/AW/TW : 39/19
ACSSAWTW | Dipper/ACSS/AW/TW | 1351.5 | 35 | 7 |  | 0.1155 | 0.3465 | 1.256 |  | 7 | 3 | 25 | 0.0689 | 75 | 0.0836 | 1273 | 210.4 | Southwire | ACSSAWTW : 1351.5 : Dipper/ACSS/AW/TW : 35/7
ACSSAWTW | Mackenzie/ACSS/AW/TW | 1359.7 | 36 | 7 |  | 0.1159 | 0.3477 | 1.259 |  | 7 | 3 | 25 | 0.0685 | 75 | 0.0831 | 1281 | 211.9 | Southwire | ACSSAWTW : 1359.7 : Mackenzie/ACSS/AW/TW : 36/7
ACSSAWTW | Truckee/ACSS/AW/TW | 1372.5 | 30 | 7 |  | 0.1004 | 0.3012 | 1.248 |  | 5 | 3 | 25 | 0.0685 | 75 | 0.083 | 1292 | 159 | Southwire | ACSSAWTW : 1372.5 : Truckee/ACSS/AW/TW : 30/7
ACSSAWTW | Thames/ACSS/AW/TW | 1334.6 | 39 | 19 |  | 0.0944 | 0.472 | 1.29 |  | 13 | 3 | 25 | 0.068 | 75 | 0.0827 | 1260 | 382.2 | Southwire | ACSSAWTW : 1334.6 : Thames/ACSS/AW/TW : 39/19
ACSSAWTW | Martin/ACSS/AW/TW | 1351.5 | 39 | 19 |  | 0.0949 | 0.4745 | 1.3 |  | 13 | 3 | 25 | 0.0672 | 75 | 0.0818 | 1276 | 386.3 | Southwire | ACSSAWTW : 1351.5 : Martin/ACSS/AW/TW : 39/19
ACSSAWTW | Bobolink/ACSS/AW/TW | 1431 | 36 | 7 |  | 0.1189 | 0.3567 | 1.291 |  | 7 | 3 | 25 | 0.0654 | 75 | 0.0792 | 1347.8 | 223 | Southwire | ACSSAWTW : 1431 : Bobolink/ACSS/AW/TW : 36/7
ACSSAWTW | MiramichiACSS/AW/TW | 1455.3 | 36 | 7 |  | 0.12 | 0.36 | 1.302 |  | 7 | 3 | 25 | 0.0644 | 75 | 0.078 | 1371 | 227.1 | Southwire | ACSSAWTW : 1455.3 : MiramichiACSS/AW/TW : 36/7
ACSSAWTW | St. Croix/ACSS/AW/TW | 1467.8 | 33 | 7 |  | 0.1041 | 0.3123 | 1.292 |  | 5 | 3 | 25 | 0.0645 | 75 | 0.0779 | 1381 | 170.9 | Southwire | ACSSAWTW : 1467.8 : St. Croix/ACSS/AW/TW : 33/7
ACSSAWTW | Plover/ACSS/AW/TW | 1431 | 39 | 19 |  | 0.0977 | 0.4885 | 1.337 |  | 13 | 3 | 25 | 0.0638 | 75 | 0.0774 | 1351 | 409.4 | Southwire | ACSSAWTW : 1431 : Plover/ACSS/AW/TW : 39/19
ACSSAWTW | Merrimack/ACSS/AW/TW | 1433.6 | 39 | 19 |  | 0.0978 | 0.489 | 1.34 |  | 13 | 3 | 25 | 0.0637 | 75 | 0.0773 | 1353.6 | 410.3 | Southwire | ACSSAWTW : 1433.6 : Merrimack/ACSS/AW/TW : 39/19
ACSSAWTW | Platte/ACSS/AW/TW | 1569 | 33 | 7 |  | 0.1074 | 0.3222 | 1.334 |  | 5 | 3 | 25 | 0.0608 | 75 | 0.0733 | 1476 | 181.9 | Southwire | ACSSAWTW : 1569 : Platte/ACSS/AW/TW : 33/7
ACSSAWTW | Potomac/ACSS/AW/TW | 1557.4 | 36 | 7 |  | 0.1241 | 0.3723 | 1.345 |  | 7 | 3 | 25 | 0.0606 | 75 | 0.0732 | 1467 | 242.9 | Southwire | ACSSAWTW : 1557.4 : Potomac/ACSS/AW/TW : 36/7
ACSSAWTW | Rio Grande/ACSS/AW/TW | 1533.3 | 39 | 19 |  | 0.1012 | 0.506 | 1.382 |  | 13 | 3 | 25 | 0.0599 | 75 | 0.0725 | 1448 | 439.3 | Southwire | ACSSAWTW : 1533.3 : Rio Grande/ACSS/AW/TW : 39/19
ACSSAWTW | Lapwing/ACSS/AW/TW | 1590 | 36 | 7 |  | 0.1253 | 0.3759 | 1.358 |  | 7 | 3 | 25 | 0.0595 | 75 | 0.0718 | 1497.6 | 247.6 | Southwire | ACSSAWTW : 1590 : Lapwing/ACSS/AW/TW : 36/7
ACSSAWTW | Falcon/ACSS/AW/TW | 1590 | 42 | 19 |  | 0.103 | 0.515 | 1.408 |  | 13 | 3 | 25 | 0.0579 | 75 | 0.0701 | 1501.3 | 455 | Southwire | ACSSAWTW : 1590 : Falcon/ACSS/AW/TW : 42/19
ACSSAWTW | Schuylkill/ACSS/AW/TW | 1657.4 | 36 | 7 |  | 0.128 | 0.384 | 1.386 |  | 7 | 3 | 25 | 0.0574 | 75 | 0.0691 | 1561 | 258.4 | Southwire | ACSSAWTW : 1657.4 : Schuylkill/ACSS/AW/TW : 36/7
ACSSAWTW | Pecos/ACSS/AW/TW | 1622 | 39 | 19 |  | 0.1064 | 0.532 | 1.424 |  | 13 | 3 | 25 | 0.0567 | 75 | 0.0686 | 1531.5 | 485.6 | Southwire | ACSSAWTW : 1622 : Pecos/ACSS/AW/TW : 39/19
ACSSAWTW | Pee Dee/ACSS/AW/TW | 1758.6 | 37 | 7 |  | 0.1319 | 0.3957 | 1.427 |  | 7 | 3 | 25 | 0.0545 | 75 | 0.0655 | 1656 | 274.4 | Southwire | ACSSAWTW : 1758.6 : Pee Dee/ACSS/AW/TW : 37/7
ACSSAWTW | James/ACSS/AW/TW | 1730.6 | 39 | 19 |  | 0.1075 | 0.5375 | 1.47 |  | 13 | 3 | 25 | 0.0537 | 75 | 0.0648 | 1634 | 495.7 | Southwire | ACSSAWTW : 1730.6 : James/ACSS/AW/TW : 39/19
ACSSAWTW | Chukar/ACSS/AW/TW | 1780 | 37 | 19 |  | 0.0874 | 0.437 | 1.445 |  | 8 | 3 | 25 | 0.0534 | 75 | 0.0643 | 1674.1 | 327.6 | Southwire | ACSSAWTW : 1780 : Chukar/ACSS/AW/TW : 37/19
ACSSAWTW | Athabaska/ACSS/AW/TW | 1949.6 | 42 | 7 |  | 0.1392 | 0.4176 | 1.504 |  | 7 | 3 | 25 | 0.0499 | 75 | 0.0587 | 1836.3 | 305.6 | Southwire | ACSSAWTW : 1949.6 : Athabaska/ACSS/AW/TW : 42/7
ACSSAWTW | Cumberland/ACSS/AW/TW | 1926.9 | 42 | 19 |  | 0.1133 | 0.5665 | 1.545 |  | 13 | 3 | 25 | 0.0488 | 75 | 0.0587 | 1819.4 | 550.6 | Southwire | ACSSAWTW : 1926.9 : Cumberland/ACSS/AW/TW : 42/19
ACSSAWTW | Powder/ACSS/AW/TW | 2153.8 | 64 | 19 |  | 0.0961 | 0.4805 | 1.602 |  | 8 | 4 | 25 | 0.0458 | 75 | 0.0536 | 2043 | 396.1 | Southwire | ACSSAWTW : 2153.8 : Powder/ACSS/AW/TW : 64/19
ACSSAWTW | Bluebird/ACSS/AW/TW | 2156 | 64 | 19 |  | 0.0961 | 0.4805 | 1.608 |  | 8 | 4 | 25 | 0.0458 | 75 | 0.0535 | 2044.6 | 396.1 | Southwire | ACSSAWTW : 2156 : Bluebird/ACSS/AW/TW : 64/19
ACSSAWTW | Santee/ACSS/AW/TW | 2627.3 | 64 | 19 |  | 0.1062 | 0.531 | 1.762 |  | 8 | 4 | 25 | 0.0391 | 75 | 0.0453 | 2492 | 483.8 | Southwire | ACSSAWTW : 2627.3 : Santee/ACSS/AW/TW : 64/19
ACSSTW | Linnet/ACSS/TW | 336.4 | 18 | 7 |  | 0.0884 | 0.2652 | 0.659 |  | 16 | 2 | 25 | 0.2647 | 75 | 0.3181 | 315.9 | 145.5 | Southwire | ACSSTW : 336.4 : Linnet/ACSS/TW : 18/7
ACSSTW | Oriole/ACSS/TW | 336.4 | 16 | 7 |  | 0.1059 | 0.3177 | 0.693 |  | 23 | 2 | 25 | 0.2622 | 75 | 0.3151 | 316.1 | 208.7 | Southwire | ACSSTW : 336.4 : Oriole/ACSS/TW : 16/7
ACSSTW | Flicker/ACSS/TW | 477 | 18 | 7 |  | 0.094 | 0.282 | 0.776 |  | 13 | 2 | 25 | 0.1877 | 75 | 0.2255 | 447.8 | 164.4 | Southwire | ACSSTW : 477 : Flicker/ACSS/TW : 18/7
ACSSTW | Hawk | 477 | 18 | 7 |  | 0.1053 | 0.3159 | 0.789 |  | 16 | 2 | 25 | 0.18691 | 75 | 0.22493 | 448.1 | 206.3 | Alcan | ACSSTW : 477 : Hawk : 18/7
ACSSTW | Hawk/ACSS/TW | 477 | 18 | 7 |  | 0.1053 | 0.3159 | 0.789 |  | 16 | 2 | 25 | 0.187 | 75 | 0.2247 | 448.1 | 206.3 | Southwire | ACSSTW : 477 : Hawk/ACSS/TW : 18/7
ACSSTW | Hen/ACSS/TW | 477 | 16 | 7 |  | 0.1261 | 0.3783 | 0.825 |  | 23 | 2 | 25 | 0.1852 | 75 | 0.2225 | 448.3 | 296 | Southwire | ACSSTW : 477 : Hen/ACSS/TW : 16/7
ACSSTW | Parakeet/ACSS/TW | 556.5 | 18 | 7 |  | 0.1015 | 0.3045 | 0.835 |  | 13 | 2 | 25 | 0.1612 | 75 | 0.1935 | 522.4 | 191.7 | Southwire | ACSSTW : 556.5 : Parakeet/ACSS/TW : 18/7
ACSSTW | Dove/ACSS/TW | 556.5 | 20 | 7 |  | 0.1138 | 0.3414 | 0.852 |  | 16 | 2 | 25 | 0.1606 | 75 | 0.1928 | 522.9 | 241 | Southwire | ACSSTW : 556.5 : Dove/ACSS/TW : 20/7
ACSSTW | Dove | 556.5 | 20 | 7 |  | 0.1138 | 0.3414 | 0.852 |  | 16 | 2 | 25 | 0.15998 | 75 | 0.19219 | 522.9 | 241 | Alcan | ACSSTW : 556.5 : Dove : 20/7
ACSSTW | Calumet/ACSS/TW | 565.3 | 20 | 7 |  | 0.1146 | 0.3441 | 0.858 |  | 16 | 2 | 25 | 0.1581 | 75 | 0.1898 | 531.2 | 244.4 | Southwire | ACSSTW : 565.3 : Calumet/ACSS/TW : 20/7
ACSSTW | Mohawk/ACSS/TW | 571.7 | 18 | 7 |  | 0.103 | 0.309 | 0.846 |  | 13 | 2 | 25 | 0.157 | 75 | 0.1884 | 536.6 | 197.4 | Southwire | ACSSTW : 571.7 : Mohawk/ACSS/TW : 18/7
ACSSTW | Rook/ACSS/TW | 636 | 18 | 7 |  | 0.1085 | 0.3255 | 0.89 |  | 13 | 2 | 25 | 0.1413 | 75 | 0.1696 | 597 | 219.1 | Southwire | ACSSTW : 636 : Rook/ACSS/TW : 18/7
ACSSTW | Grosbeak/ACSS/TW | 636 | 20 | 7 |  | 0.1216 | 0.3648 | 0.908 |  | 16 | 2 | 25 | 0.1407 | 75 | 0.1689 | 597.6 | 275.1 | Southwire | ACSSTW : 636 : Grosbeak/ACSS/TW : 20/7
ACSSTW | Grosbeak | 636 | 20 | 7 |  | 0.1216 | 0.3648 | 0.908 |  | 16 | 2 | 25 | 0.14045 | 75 | 0.16843 | 597.6 | 275.1 | Alcan | ACSSTW : 636 : Grosbeak : 20/7
ACSSTW | Scoter/ACSS/TW | 636 | 18 | 7 |  | 0.1456 | 0.4368 | 0.953 |  | 23 | 2 | 25 | 0.1393 | 75 | 0.1672 | 597.6 | 394.6 | Southwire | ACSSTW : 636 : Scoter/ACSS/TW : 18/7
ACSSTW | Mystic/ACSS/TW | 666.6 | 20 | 7 |  | 0.1111 | 0.3333 | 0.913 |  | 13 | 2 | 25 | 0.1349 | 75 | 0.1619 | 625.7 | 229.7 | Southwire | ACSSTW : 666.6 : Mystic/ACSS/TW : 20/7
ACSSTW | Oswego/ACSS/TW | 664.8 | 20 | 7 |  | 0.1244 | 0.3732 | 0.927 |  | 16 | 2 | 25 | 0.1347 | 75 | 0.1617 | 624.6 | 288 | Southwire | ACSSTW : 664.8 : Oswego/ACSS/TW : 20/7
ACSSTW | Wabash/ACSS/TW | 762.8 | 20 | 7 |  | 0.1331 | 0.3993 | 0.99 |  | 16 | 2 | 25 | 0.1177 | 75 | 0.1411 | 716.7 | 330 | Southwire | ACSSTW : 762.8 : Wabash/ACSS/TW : 20/7
ACSSTW | Maumee/ACSS/TW | 768.2 | 20 | 7 |  | 0.1195 | 0.3585 | 0.977 |  | 13 | 2 | 25 | 0.1174 | 75 | 0.1407 | 721.1 | 265.7 | Southwire | ACSSTW : 768.2 : Maumee/ACSS/TW : 20/7
ACSSTW | Tern/ACSS/TW | 795 | 17 | 7 |  | 0.0886 | 0.2658 | 0.96 |  | 7 | 2 | 25 | 0.1147 | 75 | 0.1373 | 745.2 | 146.1 | Southwire | ACSSTW : 795 : Tern/ACSS/TW : 17/7
ACSSTW | Puffin/ACSS/TW | 795 | 18 | 7 |  | 0.1108 | 0.3324 | 0.98 |  | 10 | 2 | 25 | 0.1139 | 75 | 0.1365 | 745.9 | 228.4 | Southwire | ACSSTW : 795 : Puffin/ACSS/TW : 18/7
ACSSTW | Condor/ACSS/TW | 795 | 20 | 7 |  | 0.1213 | 0.3639 | 0.993 |  | 13 | 2 | 25 | 0.1136 | 75 | 0.1361 | 746.3 | 273.9 | Southwire | ACSSTW : 795 : Condor/ACSS/TW : 20/7
ACSSTW | Drake/ACSS/TW | 795 | 20 | 7 |  | 0.136 | 0.408 | 1.01 |  | 16 | 2 | 25 | 0.113 | 75 | 0.1355 | 747 | 344.2 | Southwire | ACSSTW : 795 : Drake/ACSS/TW : 20/7
ACSSTW | Drake | 795 | 20 | 7 |  | 0.136 | 0.408 | 1.01 |  | 16 | 2 | 25 | 0.11246 | 75 | 0.13464 | 747 | 344.2 | Alcan | ACSSTW : 795 : Drake : 20/7
ACSSTW | Canary/ACSS/TW | 900 | 20 | 7 |  | 0.1291 | 0.3873 | 1.055 |  | 13 | 3 | 25 | 0.1007 | 75 | 0.1205 | 844.9 | 310.2 | Southwire | ACSSTW : 900 : Canary/ACSS/TW : 20/7
ACSSTW | Phoenix/ACSS/TW | 954 | 30 | 7 |  | 0.0837 | 0.2511 | 1.044 |  | 5 | 3 | 25 | 0.097 | 75 | 0.119 | 897.7 | 130.4 | Southwire | ACSSTW : 954 : Phoenix/ACSS/TW : 30/7
ACSSTW | Fraser/ACSS/TW | 946.7 | 35 | 7 |  | 0.1154 | 0.3462 | 1.077 |  | 10 | 3 | 25 | 0.0969 | 75 | 0.119 | 892.6 | 248 | Southwire | ACSSTW : 946.7 : Fraser/ACSS/TW : 35/7
ACSSTW | Rail/ACSS/TW | 954 | 32 | 7 |  | 0.0971 | 0.2913 | 1.061 |  | 7 | 3 | 25 | 0.0967 | 75 | 0.1187 | 898.6 | 175 | Southwire | ACSSTW : 954 : Rail/ACSS/TW : 32/7
ACSSTW | Kettle/ACSS/TW | 957.2 | 32 | 7 |  | 0.0973 | 0.2919 | 1.06 |  | 7 | 3 | 25 | 0.0964 | 75 | 0.1183 | 901.6 | 176.2 | Southwire | ACSSTW : 957.2 : Kettle/ACSS/TW : 32/7
ACSSTW | Cardinal/ACSS/TW | 954 | 20 | 7 |  | 0.1329 | 0.3987 | 1.084 |  | 13 | 2 | 25 | 0.0952 | 75 | 0.1138 | 895.5 | 328.7 | Southwire | ACSSTW : 954 : Cardinal/ACSS/TW : 20/7
ACSSTW | Cardinal | 954 | 20 | 7 |  | 0.1329 | 0.3987 | 1.084 |  | 13 | 2 | 25 | 0.09451 | 75 | 0.11299 | 895.5 | 328.7 | Alcan | ACSSTW : 954 : Cardinal : 20/7
ACSSTW | Suwannee/ACSS/TW | 959.6 | 22 | 7 |  | 0.1493 | 0.4479 | 1.108 |  | 16 | 2 | 25 | 0.0941 | 75 | 0.1127 | 901.6 | 415 | Southwire | ACSSTW : 959.6 : Suwannee/ACSS/TW : 22/7
ACSSTW | Columbia/ACSS/TW | 966.2 | 21 | 7 |  | 0.1338 | 0.4014 | 1.092 |  | 13 | 2 | 25 | 0.094 | 75 | 0.1124 | 906.9 | 333.2 | Southwire | ACSSTW : 966.2 : Columbia/ACSS/TW : 21/7
ACSSTW | Snowbird/ACSS/TW | 1033.5 | 30 | 7 |  | 0.0871 | 0.2613 | 1.089 |  | 5 | 3 | 25 | 0.0899 | 75 | 0.1101 | 972.5 | 141.2 | Southwire | ACSSTW : 1033.5 : Snowbird/ACSS/TW : 30/7
ACSSTW | Ortolan/ACSS/TW | 1033.5 | 32 | 7 |  | 0.101 | 0.303 | 1.102 |  | 7 | 3 | 25 | 0.0896 | 75 | 0.1098 | 972.5 | 189.8 | Southwire | ACSSTW : 1033.5 : Ortolan/ACSS/TW : 32/7
ACSSTW | Curlew/ACSS/TW | 1033.5 | 20 | 7 |  | 0.1383 | 0.4149 | 1.129 |  | 13 | 2 | 25 | 0.0881 | 75 | 0.1053 | 970.1 | 356 | Southwire | ACSSTW : 1033.5 : Curlew/ACSS/TW : 20/7
ACSSTW | Curlew | 1033.5 | 20 | 7 |  | 0.1383 | 0.4149 | 1.129 |  | 13 | 2 | 25 | 0.08818 | 75 | 0.10507 | 970.1 | 356 | Alcan | ACSSTW : 1033.5 : Curlew : 20/7
ACSSTW | Finch/ACSS/TW | 1113 | 38 | 19 |  | 0.0862 | 0.431 | 1.185 |  | 13 | 3 | 25 | 0.0826 | 75 | 0.1012 | 1051 | 376.1 | Southwire | ACSSTW : 1113 : Finch/ACSS/TW : 38/19
ACSSTW | Genesee/ACSS/TW | 1158 | 33 | 7 |  | 0.1078 | 0.3234 | 1.165 |  | 7 | 3 | 25 | 0.0805 | 75 | 0.0983 | 1091 | 216 | Southwire | ACSSTW : 1158 : Genesee/ACSS/TW : 33/7
ACSSTW | Cheyenne/ACSS/TW | 1168.1 | 30 | 7 |  | 0.0926 | 0.2778 | 1.155 |  | 5 | 3 | 25 | 0.0801 | 75 | 0.0979 | 1099 | 159.6 | Southwire | ACSSTW : 1168.1 : Cheyenne/ACSS/TW : 30/7
ACSSTW | Oxbird/ACSS/TW | 1192.5 | 30 | 7 |  | 0.0936 | 0.2808 | 1.167 |  | 5 | 3 | 25 | 0.0786 | 75 | 0.096 | 1122 | 163 | Southwire | ACSSTW : 1192.5 : Oxbird/ACSS/TW : 30/7
ACSSTW | Bunting/ACSS/TW | 1192.5 | 33 | 7 |  | 0.1085 | 0.3255 | 1.181 |  | 7 | 3 | 25 | 0.0783 | 75 | 0.0956 | 1123 | 219.1 | Southwire | ACSSTW : 1192.5 : Bunting/ACSS/TW : 33/7
ACSSTW | Grackle/ACSS/TW | 1192.5 | 38 | 19 |  | 0.0892 | 0.446 | 1.225 |  | 13 | 3 | 25 | 0.0773 | 75 | 0.0947 | 1126 | 403 | Southwire | ACSSTW : 1192.5 : Grackle/ACSS/TW : 38/19
ACSSTW | Hudson/ACSS/TW | 1158.4 | 25 | 7 |  | 0.1467 | 0.4401 | 1.196 |  | 13 | 2 | 25 | 0.079 | 75 | 0.0943 | 1087 | 400 | Southwire | ACSSTW : 1158.4 : Hudson/ACSS/TW : 25/7
ACSSTW | Avocet/ACSS/TW | 1113 | 30 | 7 |  | 0.0904 | 0.2712 | 1.129 |  | 5 | 3 | 25 | 0.0838 | 75 | 0.0938 | 1047 | 152.1 | Southwire | ACSSTW : 1113 : Avocet/ACSS/TW : 30/7
ACSSTW | Bluejay/ACSS/TW | 1113 | 33 | 7 |  | 0.1049 | 0.3147 | 1.143 |  | 7 | 3 | 25 | 0.0835 | 75 | 0.0935 | 1048 | 204.8 | Southwire | ACSSTW : 1113 : Bluejay/ACSS/TW : 33/7
ACSSTW | Yukon/ACSS/TW | 1233.6 | 38 | 19 |  | 0.091 | 0.455 | 1.245 |  | 13 | 3 | 25 | 0.0749 | 75 | 0.0916 | 1166.5 | 419.5 | Southwire | ACSSTW : 1233.6 : Yukon/ACSS/TW : 38/19
ACSSTW | Nelson/ACSS/TW | 1257.1 | 35 | 7 |  | 0.1115 | 0.3345 | 1.213 |  | 7 | 3 | 25 | 0.0745 | 75 | 0.0909 | 1184 | 231.3 | Southwire | ACSSTW : 1257.1 : Nelson/ACSS/TW : 35/7
ACSSTW | Catawba/ACSS/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0741 | 75 | 0.0902 | 1197 | 174 | Southwire | ACSSTW : 1272 : Catawba/ACSS/TW : 30/7
ACSSTW | Scissortail/ACSS/TW | 1272 | 30 | 7 |  | 0.0967 | 0.2901 | 1.203 |  | 5 | 3 | 25 | 0.0741 | 75 | 0.0902 | 1198 | 174 | Southwire | ACSSTW : 1272 : Scissortail/ACSS/TW : 30/7
ACSSTW | Bittern/ACSS/TW | 1272 | 35 | 7 |  | 0.1121 | 0.3363 | 1.22 |  | 7 | 3 | 25 | 0.0737 | 75 | 0.0899 | 1198 | 233.9 | Southwire | ACSSTW : 1272 : Bittern/ACSS/TW : 35/7
ACSSTW | Pheasant/ACSS/TW | 1272 | 39 | 19 |  | 0.0921 | 0.4605 | 1.264 |  | 13 | 3 | 25 | 0.0728 | 75 | 0.089 | 1201 | 430 | Southwire | ACSSTW : 1272 : Pheasant/ACSS/TW : 39/19
ACSSTW | Yukon | 1233.6 | 38 | 19 |  | 0.091 | 0.455 | 1.245 |  | 13 | 3 | 25 | 0.07498 | 75 | 0.0887 | 1166.5 | 419.5 | Alcan | ACSSTW : 1233.6 : Yukon : 38/19
ACSSTW | Pheasant | 1272 | 39 | 19 |  | 0.0921 | 0.4605 | 1.264 |  | 13 | 3 | 25 | 0.07286 | 75 | 0.08659 | 1201 | 430 | Alcan | ACSSTW : 1272 : Pheasant : 39/19
ACSSTW | Dipper/ACSS/TW | 1351.5 | 35 | 7 |  | 0.1155 | 0.3465 | 1.256 |  | 7 | 3 | 25 | 0.0697 | 75 | 0.0849 | 1273 | 248.3 | Southwire | ACSSTW : 1351.5 : Dipper/ACSS/TW : 35/7
ACSSTW | Thames/ACSS/TW | 1334.6 | 39 | 19 |  | 0.0944 | 0.472 | 1.29 |  | 13 | 3 | 25 | 0.0696 | 75 | 0.0849 | 1260 | 451.4 | Southwire | ACSSTW : 1334.6 : Thames/ACSS/TW : 39/19
ACSSTW | Mackenzie/ACSS/TW | 1359.7 | 36 | 7 |  | 0.1159 | 0.3477 | 1.259 |  | 7 | 3 | 25 | 0.0694 | 75 | 0.0844 | 1281 | 250 | Southwire | ACSSTW : 1359.7 : Mackenzie/ACSS/TW : 36/7
ACSSTW | Truckee/ACSS/TW | 1372.5 | 30 | 7 |  | 0.1004 | 0.3012 | 1.248 |  | 5 | 3 | 25 | 0.0691 | 75 | 0.084 | 1292 | 187.6 | Southwire | ACSSTW : 1372.5 : Truckee/ACSS/TW : 30/7
ACSSTW | Martin/ACSS/TW | 1351.5 | 39 | 19 |  | 0.0949 | 0.4745 | 1.3 |  | 13 | 3 | 25 | 0.0688 | 75 | 0.0839 | 1276 | 456 | Southwire | ACSSTW : 1351.5 : Martin/ACSS/TW : 39/19
ACSSTW | Bobolink/ACSS/TW | 1431 | 36 | 7 |  | 0.1189 | 0.3567 | 1.291 |  | 7 | 3 | 25 | 0.0662 | 75 | 0.0804 | 1347 | 263.1 | Southwire | ACSSTW : 1431 : Bobolink/ACSS/TW : 36/7
ACSSTW | Plover/ACSS/TW | 1431 | 39 | 19 |  | 0.0977 | 0.4885 | 1.337 |  | 13 | 3 | 25 | 0.0652 | 75 | 0.0795 | 1351 | 483 | Southwire | ACSSTW : 1431 : Plover/ACSS/TW : 39/19
ACSSTW | Merrimack/ACSS/TW | 1433.6 | 39 | 19 |  | 0.0978 | 0.489 | 1.34 |  | 13 | 3 | 25 | 0.0651 | 75 | 0.0793 | 1354 | 484.2 | Southwire | ACSSTW : 1433.6 : Merrimack/ACSS/TW : 39/19
ACSSTW | MiramichiACSS/TW | 1455.3 | 36 | 7 |  | 0.12 | 0.36 | 1.302 |  | 7 | 3 | 25 | 0.0652 | 75 | 0.0792 | 1371 | 268 | Southwire | ACSSTW : 1455.3 : MiramichiACSS/TW : 36/7
ACSSTW | St. Croix/ACSS/TW | 1467.8 | 33 | 7 |  | 0.1041 | 0.3123 | 1.292 |  | 5 | 3 | 25 | 0.065 | 75 | 0.0789 | 1381 | 202 | Southwire | ACSSTW : 1467.8 : St. Croix/ACSS/TW : 33/7
ACSSTW | Rio Grande/ACSS/TW | 1533.3 | 39 | 19 |  | 0.1012 | 0.506 | 1.382 |  | 13 | 3 | 25 | 0.0612 | 75 | 0.0744 | 1448 | 519 | Southwire | ACSSTW : 1533.3 : Rio Grande/ACSS/TW : 39/19
ACSSTW | Potomac/ACSS/TW | 1557.4 | 36 | 7 |  | 0.1241 | 0.3723 | 1.345 |  | 7 | 3 | 25 | 0.0613 | 75 | 0.0743 | 1467 | 287 | Southwire | ACSSTW : 1557.4 : Potomac/ACSS/TW : 36/7
ACSSTW | Platte/ACSS/TW | 1569 | 33 | 7 |  | 0.1074 | 0.3222 | 1.334 |  | 5 | 3 | 25 | 0.0613 | 75 | 0.0742 | 1476 | 215 | Southwire | ACSSTW : 1569 : Platte/ACSS/TW : 33/7
ACSSTW | Lapwing/ACSS/TW | 1590 | 36 | 7 |  | 0.1253 | 0.3759 | 1.358 |  | 7 | 3 | 25 | 0.0602 | 75 | 0.0729 | 1498 | 292 | Southwire | ACSSTW : 1590 : Lapwing/ACSS/TW : 36/7
ACSSTW | Falcon/ACSS/TW | 1590 | 42 | 19 |  | 0.103 | 0.515 | 1.408 |  | 13 | 3 | 25 | 0.0592 | 75 | 0.0719 | 1501 | 537 | Southwire | ACSSTW : 1590 : Falcon/ACSS/TW : 42/19
ACSSTW | Pecos/ACSS/TW | 1622 | 39 | 19 |  | 0.1064 | 0.532 | 1.424 |  | 13 | 3 | 25 | 0.058 | 75 | 0.0705 | 1532 | 574 | Southwire | ACSSTW : 1622 : Pecos/ACSS/TW : 39/19
ACSSTW | Lapwing | 1590 | 36 | 7 |  | 0.1253 | 0.3759 | 1.358 |  | 7 | 3 | 25 | 0.05966 | 75 | 0.07022 | 1498 | 292 | Alcan | ACSSTW : 1590 : Lapwing : 36/7
ACSSTW | Falcon | 1590 | 42 | 19 |  | 0.103 | 0.515 | 1.408 |  | 13 | 3 | 25 | 0.05914 | 75 | 0.07022 | 1501 | 537 | Alcan | ACSSTW : 1590 : Falcon : 42/19
ACSSTW | Schuylkill/ACSS/TW | 1657.4 | 36 | 7 |  | 0.128 | 0.384 | 1.386 |  | 7 | 3 | 25 | 0.0581 | 75 | 0.0702 | 1561 | 305 | Southwire | ACSSTW : 1657.4 : Schuylkill/ACSS/TW : 36/7
ACSSTW | Pee Dee/ACSS/TW | 1758.6 | 37 | 7 |  | 0.1319 | 0.3957 | 1.427 |  | 7 | 3 | 25 | 0.0551 | 75 | 0.0665 | 1656 | 324 | Southwire | ACSSTW : 1758.6 : Pee Dee/ACSS/TW : 37/7
ACSSTW | James/ACSS/TW | 1730.6 | 39 | 19 |  | 0.1075 | 0.5375 | 1.47 |  | 13 | 3 | 25 | 0.0549 | 75 | 0.0664 | 1634 | 585 | Southwire | ACSSTW : 1730.6 : James/ACSS/TW : 39/19
ACSSTW | Chukar/ACSS/TW | 1780 | 37 | 19 |  | 0.0874 | 0.437 | 1.445 |  | 8 | 3 | 25 | 0.0542 | 75 | 0.0654 | 1675 | 386.7 | Southwire | ACSSTW : 1780 : Chukar/ACSS/TW : 37/19
ACSSTW | Cumberland/ACSS/TW | 1926.9 | 42 | 19 |  | 0.1133 | 0.5665 | 1.545 |  | 13 | 3 | 25 | 0.0499 | 75 | 0.0602 | 1819 | 649.8 | Southwire | ACSSTW : 1926.9 : Cumberland/ACSS/TW : 42/19
ACSSTW | Athabaska/ACSS/TW | 1949.6 | 42 | 7 |  | 0.1392 | 0.4176 | 1.504 |  | 7 | 3 | 25 | 0.0505 | 75 | 0.0595 | 1836 | 361 | Southwire | ACSSTW : 1949.6 : Athabaska/ACSS/TW : 42/7
ACSSTW | Athabaska | 1949.6 | 42 | 7 |  | 0.1392 | 0.4176 | 1.504 |  | 7 | 3 | 25 | 0.05069 | 75 | 0.05914 | 1836 | 361 | Alcan | ACSSTW : 1949.6 : Athabaska : 42/7
ACSSTW | Cumberland | 1926.9 | 42 | 19 |  | 0.1133 | 0.5665 | 1.545 |  | 13 | 3 | 25 | 0.05016 | 75 | 0.05861 | 1819 | 649.8 | Alcan | ACSSTW : 1926.9 : Cumberland : 42/19
ACSSTW | Powder/ACSS/TW | 2153.8 | 64 | 19 |  | 0.0961 | 0.4805 | 1.602 |  | 8 | 4 | 25 | 0.0464 | 75 | 0.0543 | 2043 | 467.5 | Southwire | ACSSTW : 2153.8 : Powder/ACSS/TW : 64/19
ACSSTW | Bluebird/ACSS/TW | 2156 | 64 | 19 |  | 0.0961 | 0.4805 | 1.608 |  | 8 | 4 | 25 | 0.0464 | 75 | 0.0543 | 2045 | 467.5 | Southwire | ACSSTW : 2156 : Bluebird/ACSS/TW : 64/19
ACSSTW | Chukar | 1780 | 37 | 19 |  | 0.0874 | 0.437 | 1.445 |  | 8 | 3 | 25 | 0.05438 | 75 | 0.05396 | 1675 | 386.7 | Alcan | ACSSTW : 1780 : Chukar : 37/19
ACSSTW | Santee/ACSS/TW | 2627.3 | 64 | 19 |  | 0.1062 | 0.531 | 1.762 |  | 8 | 4 | 25 | 0.0396 | 75 | 0.0459 | 2492 | 571 | Southwire | ACSSTW : 2627.3 : Santee/ACSS/TW : 64/19
Alumoweld | 3 No. 10 | 31.15 | 3 |  | 0.1019 |  |  | 0.22 |  |  |  | 25 | 8.87 | 75 | 10.67 | 70.4 |  | Southwire | Alumoweld : 31.15 : 3 No. 10 : 3
Alumoweld | 3 No. 9 | 39.28 | 3 |  | 0.1144 |  |  | 0.247 |  |  |  | 25 | 7.04 | 75 | 8.52 | 88.8 |  | Southwire | Alumoweld : 39.28 : 3 No. 9 : 3
Alumoweld | 3 No. 8 | 49.53 | 3 |  | 0.1285 |  |  | 0.277 |  |  |  | 25 | 5.58 | 75 | 6.82 | 112 |  | Southwire | Alumoweld : 49.53 : 3 No. 8 : 3
Alumoweld | 3 No. 7 | 62.45 | 3 |  | 0.1443 |  |  | 0.311 |  |  |  | 25 | 4.42 | 75 | 5.47 | 141.2 |  | Southwire | Alumoweld : 62.45 : 3 No. 7 : 3
Alumoweld | 7 No. 10 | 72.68 | 7 |  | 0.1019 |  |  | 0.306 |  |  |  | 25 | 3.88 | 75 | 4.73 | 164.7 |  | Southwire | Alumoweld : 72.68 : 7 No. 10 : 7
Alumoweld | 3 No. 6 | 78.75 | 3 |  | 0.162 |  |  | 0.349 |  |  |  | 25 | 3.51 | 75 | 4.41 | 178.1 |  | Southwire | Alumoweld : 78.75 : 3 No. 6 : 3
Alumoweld | 7 No. 9 | 91.65 | 7 |  | 0.1144 |  |  | 0.343 |  |  |  | 25 | 3.08 | 75 | 3.8 | 207.6 |  | Southwire | Alumoweld : 91.65 : 7 No. 9 : 7
Alumoweld | 3 No. 5 | 99.31 | 3 |  | 0.1819 |  |  | 0.392 |  |  |  | 25 | 2.78 | 75 | 3.56 | 224.5 |  | Southwire | Alumoweld : 99.31 : 3 No. 5 : 3
Alumoweld | 7 No. 8 | 115.6 | 7 |  | 0.1285 |  |  | 0.385 |  |  |  | 25 | 2.44 | 75 | 3.06 | 261.8 |  | Southwire | Alumoweld : 115.6 : 7 No. 8 : 7
Alumoweld | 7 No. 7 | 145.7 | 7 |  | 0.1443 |  |  | 0.433 |  |  |  | 25 | 1.937 | 75 | 2.47 | 330 |  | Southwire | Alumoweld : 145.7 : 7 No. 7 : 7
Alumoweld | 7 No. 6 | 183.8 | 7 |  | 0.162 |  |  | 0.486 |  |  |  | 25 | 1.536 | 75 | 2.01 | 416.3 |  | Southwire | Alumoweld : 183.8 : 7 No. 6 : 7
Alumoweld | 19 No. 10 | 197.3 | 19 |  | 0.1019 |  |  | 0.509 |  |  |  | 25 | 1.437 | 75 | 1.896 | 448.7 |  | Southwire | Alumoweld : 197.3 : 19 No. 10 : 19
Alumoweld | 7 No. 5 | 231.7 | 7 |  | 0.1819 |  |  | 0.546 |  |  |  | 25 | 1.24 | 75 | 1.669 | 524.9 |  | Southwire | Alumoweld : 231.7 : 7 No. 5 : 7
Alumoweld | 19 No. 9 | 248.8 | 19 |  | 0.1144 |  |  | 0.572 |  |  |  | 25 | 1.14 | 75 | 1.554 | 565.8 |  | Southwire | Alumoweld : 248.8 : 19 No. 9 : 19
Alumoweld | 19 No. 8 | 313.7 | 19 |  | 0.1285 |  |  | 0.642 |  |  |  | 25 | 0.9038 | 75 | 1.28 | 713.5 |  | Southwire | Alumoweld : 313.7 : 19 No. 8 : 19
Alumoweld | 37 No. 10 | 384.2 | 37 |  | 0.1019 |  |  | 0.713 |  |  |  | 25 | 0.7409 | 75 | 1.093 | 879 |  | Southwire | Alumoweld : 384.2 : 37 No. 10 : 37
Alumoweld | 19 No. 7 | 395.5 | 19 |  | 0.1443 |  |  | 0.721 |  |  |  | 25 | 0.7171 | 75 | 1.064 | 899.5 |  | Southwire | Alumoweld : 395.5 : 19 No. 7 : 19
Alumoweld | 37 No. 9 | 484.4 | 37 |  | 0.1144 |  |  | 0.801 |  |  |  | 25 | 0.5886 | 75 | 0.9144 | 1108 |  | Southwire | Alumoweld : 484.4 : 37 No. 9 : 37
Alumoweld | 19 No. 6 | 498.8 | 19 |  | 0.162 |  |  | 0.81 |  |  |  | 25 | 0.5683 | 75 | 0.8886 | 1134 |  | Southwire | Alumoweld : 498.8 : 19 No. 6 : 19
Alumoweld | 37 No. 8 | 610.9 | 37 |  | 0.1285 |  |  | 0.899 |  |  |  | 25 | 0.4667 | 75 | 0.7679 | 1398 |  | Southwire | Alumoweld : 610.9 : 37 No. 8 : 37
Alumoweld | 19 No. 5 | 628.9 | 19 |  | 0.1819 |  |  | 0.91 |  |  |  | 25 | 0.4507 | 75 | 0.7585 | 1430 |  | Southwire | Alumoweld : 628.9 : 19 No. 5 : 19
Alumoweld | 37 No. 7 | 770.3 | 37 |  | 0.1443 |  |  | 1.01 |  |  |  | 25 | 0.3702 | 75 | 0.6524 | 1762 |  | Southwire | Alumoweld : 770.3 : 37 No. 7 : 37
Alumoweld | 37 No. 6 | 971.3 | 37 |  | 0.162 |  |  | 1.13 |  |  |  | 25 | 0.2935 | 75 | 0.5546 | 2222 |  | Southwire | Alumoweld : 971.3 : 37 No. 6 : 37
Alumoweld | 37 No. 5 | 1225 | 37 |  | 0.1819 |  |  | 1.27 |  |  |  | 25 | 0.2327 | 75 | 0.4788 | 2802 |  | Southwire | Alumoweld : 1225 : 37 No. 5 : 37
HD Copper | 8 - 1 | 8 | 1 |  | 0.1285 |  |  | 0.1285 |  |  |  | 25 | 3.5146 | 75 | 4.1682 | 49.98 |  | Southwire | HD Copper : 8 : 8 - 1 : 1
HD Copper | 7 - 1 | 7 | 1 |  | 0.1443 |  |  | 0.1443 |  |  |  | 25 | 2.787 | 75 | 3.3053 | 63.03 |  | Southwire | HD Copper : 7 : 7 - 1 : 1
HD Copper | 6 - 7 | 6 | 7 |  | 0.0612 |  |  | 0.1836 |  |  |  | 25 | 2.2556 | 75 | 2.6751 | 81 |  | Southwire | HD Copper : 6 : 6 - 7 : 7
HD Copper | 6 - 1 | 6 | 1 |  | 0.162 |  |  | 0.162 |  |  |  | 25 | 2.2114 | 75 | 2.6226 | 79.44 |  | Southwire | HD Copper : 6 : 6 - 1 : 1
HD Copper | 5 - 1 | 5 | 1 |  | 0.1819 |  |  | 0.1819 |  |  |  | 25 | 1.7537 | 75 | 2.0798 | 100.2 |  | Southwire | HD Copper : 5 : 5 - 1 : 1
HD Copper | 4 - 7 | 4 | 7 |  | 0.0772 |  |  | 0.2316 |  |  |  | 25 | 1.4182 | 75 | 1.6818 | 128.9 |  | Southwire | HD Copper : 4 : 4 - 7 : 7
HD Copper | 4 - 3 | 4 | 3 |  | 0.118 |  |  | 0.25429 |  |  |  | 25 | 1.4043 | 75 | 1.6653 | 127.6 |  | Southwire | HD Copper : 4 : 4 - 3 : 3
HD Copper | 4 - 1 | 4 | 1 |  | 0.2043 |  |  | 0.2043 |  |  |  | 25 | 1.3904 | 75 | 1.6488 | 126.3 |  | Southwire | HD Copper : 4 : 4 - 1 : 1
HD Copper | 3 - 7 | 3 | 7 |  | 0.0867 |  |  | 0.2601 |  |  |  | 25 | 1.125 | 75 | 1.3342 | 162.4609 |  | Southwire | HD Copper : 3 : 3 - 7 : 7
HD Copper | 3 - 3 | 3 | 3 |  | 0.1325 |  |  | 0.28554 |  |  |  | 25 | 1.114 | 75 | 1.3211 | 160.9 |  | Southwire | HD Copper : 3 : 3 - 3 : 3
HD Copper | 3 - 1 | 3 | 1 |  | 0.2294 |  |  | 0.2294 |  |  |  | 25 | 1.103 | 75 | 1.308 | 159.3 |  | Southwire | HD Copper : 3 : 3 - 1 : 1
HD Copper | 2 - 7 | 2 | 7 |  | 0.0974 |  |  | 0.2922 |  |  |  | 25 | 0.8922 | 75 | 1.058 | 204.9 |  | Southwire | HD Copper : 2 : 2 - 7 : 7
HD Copper | 2 - 3 | 2 | 3 |  | 0.1487 |  |  | 0.32045 |  |  |  | 25 | 0.8835 | 75 | 1.0477 | 202.9 |  | Southwire | HD Copper : 2 : 2 - 3 : 3
HD Copper | 2 - 1 | 2 | 1 |  | 0.2576 |  |  | 0.2576 |  |  |  | 25 | 0.8747 | 75 | 1.0373 | 200.9 |  | Southwire | HD Copper : 2 : 2 - 1 : 1
HD Copper | 1 - 7 | 1 | 7 |  | 0.1093 |  |  | 0.3279 |  |  |  | 25 | 0.7076 | 75 | 0.8391 | 258.4 |  | Southwire | HD Copper : 1 : 1 - 7 : 7
HD Copper | 1 - 3 | 1 | 3 |  | 0.167 |  |  | 0.35989 |  |  |  | 25 | 0.7007 | 75 | 0.8309 | 255.9 |  | Southwire | HD Copper : 1 : 1 - 3 : 3
HD Copper | 1 - 1 | 1 | 1 |  | 0.2893 |  |  | 0.2893 |  |  |  | 25 | 0.6938 | 75 | 0.8226 | 253.3 |  | Southwire | HD Copper : 1 : 1 - 1 : 1
HD Copper | 1/0 - 7 | 1/0 | 7 |  | 0.1228 |  |  | 0.3684 |  |  |  | 25 | 0.561 | 75 | 0.6652 | 325.9173 |  | Southwire | HD Copper : 1/0 : 1/0 - 7 : 7
HD Copper | 1/0 - 19 | 1/0 | 19 |  | 0.0745 |  |  | 0.3725 |  |  |  | 25 | 0.561 | 75 | 0.6652 | 325.5958 |  | Southwire | HD Copper : 1/0 : 1/0 - 19 : 19
HD Copper | 1/0 - 1 | 1/0 | 1 |  | 0.3249 |  |  | 0.3249 |  |  |  | 25 | 0.55 | 75 | 0.6521 | 319.5 |  | Southwire | HD Copper : 1/0 : 1/0 - 1 : 1
HD Copper | 2/0 - 19 | 2/0 | 19 |  | 0.0837 |  |  | 0.4185 |  |  |  | 25 | 0.4454 | 75 | 0.528 | 410.9766 |  | Southwire | HD Copper : 2/0 : 2/0 - 19 : 19
HD Copper | 2/0 - 7 | 2/0 | 7 |  | 0.1379 |  |  | 0.4137 |  |  |  | 25 | 0.4454 | 75 | 0.528 | 410.9975 |  | Southwire | HD Copper : 2/0 : 2/0 - 7 : 7
HD Copper | 2/0 - 1 | 2/0 | 1 |  | 0.3648 |  |  | 0.3648 |  |  |  | 25 | 0.4322 | 75 | 0.513 | 402.6 |  | Southwire | HD Copper : 2/0 : 2/0 - 1 : 1
HD Copper | 3/0 - 19 | 3/0 | 19 |  | 0.0904 |  |  | 0.452 |  |  |  | 25 | 0.3536 | 75 | 0.4191 | 518.3 |  | Southwire | HD Copper : 3/0 : 3/0 - 19 : 19
HD Copper | 3/0 - 12 | 3/0 | 12 |  | 0.1183 |  |  | 0.49154 |  |  |  | 25 | 0.3536 | 75 | 0.4191 | 518.5174 |  | Southwire | HD Copper : 3/0 : 3/0 - 12 : 12
HD Copper | 3/0 - 7 | 3/0 | 7 |  | 0.1548 |  |  | 0.4644 |  |  |  | 25 | 0.3536 | 75 | 0.4191 | 517.9079 |  | Southwire | HD Copper : 3/0 : 3/0 - 7 : 7
HD Copper | 3/0 - 1 | 3/0 | 1 |  | 0.4096 |  |  | 0.4096 |  |  |  | 25 | 0.3432 | 75 | 0.4072 | 507.8 |  | Southwire | HD Copper : 3/0 : 3/0 - 1 : 1
HD Copper |  | 4/0 | 7 |  | 0.1739 |  |  | 0.522 |  |  |  | 20 | 0.27561 | 100 | 0.34851 | 653.3 |  | Old Pjm | HD Copper : 4/0 : : 7
HD Copper | 4/0 - 19 | 4/0 | 19 |  | 0.1055 |  |  | 0.5275 |  |  |  | 25 | 0.2808 | 75 | 0.3327 | 652.9367 |  | Southwire | HD Copper : 4/0 : 4/0 - 19 : 19
HD Copper | 4/0 - 12 | 4/0 | 12 |  | 0.1328 |  |  | 0.55178 |  |  |  | 25 | 0.2808 | 75 | 0.3327 | 653.4163 |  | Southwire | HD Copper : 4/0 : 4/0 - 12 : 12
HD Copper | 4/0 - 7 | 4/0 | 7 |  | 0.1739 |  |  | 0.5217 |  |  |  | 25 | 0.2808 | 75 | 0.3327 | 653.5966 |  | Southwire | HD Copper : 4/0 : 4/0 - 7 : 7
HD Copper | 4/0 - 1 | 4/0 | 1 |  | 0.46 |  |  | 0.46 |  |  |  | 25 | 0.2726 | 75 | 0.3233 | 640.5 |  | Southwire | HD Copper : 4/0 : 4/0 - 1 : 1
HD Copper | 250 - 37 | 250 | 37 |  | 0.0822 |  |  | 0.5754 |  |  |  | 25 | 0.2381 | 75 | 0.2819 | 771.8945 |  | Southwire | HD Copper : 250 : 250 - 37 : 37
HD Copper | 250 - 19 | 250 | 19 |  | 0.1147 |  |  | 0.5735 |  |  |  | 25 | 0.2381 | 75 | 0.2819 | 771.7791 |  | Southwire | HD Copper : 250 : 250 - 19 : 19
HD Copper | 250 - 12 | 250 | 12 |  | 0.1443 |  |  | 0.59957 |  |  |  | 25 | 0.2381 | 75 | 0.2819 | 771.4832 |  | Southwire | HD Copper : 250 : 250 - 12 : 12
HD Copper | 300 - 37 | 300 | 37 |  | 0.09 |  |  | 0.63 |  |  |  | 25 | 0.1989 | 75 | 0.2353 | 925.3357 |  | Southwire | HD Copper : 300 : 300 - 37 : 37
HD Copper | 300 - 19 | 300 | 19 |  | 0.1257 |  |  | 0.6285 |  |  |  | 25 | 0.1989 | 75 | 0.2353 | 926.9083 |  | Southwire | HD Copper : 300 : 300 - 19 : 19
HD Copper | 300 - 12 | 300 | 12 |  | 0.1581 |  |  | 0.65691 |  |  |  | 25 | 0.1989 | 75 | 0.2353 | 926.0993 |  | Southwire | HD Copper : 300 : 300 - 12 : 12
HD Copper | 350 - 37 | 350 | 37 |  | 0.0973 |  |  | 0.6811 |  |  |  | 25 | 0.1709 | 75 | 0.2021 | 1081.5336 |  | Southwire | HD Copper : 350 : 350 - 37 : 37
HD Copper | 350 - 19 | 350 | 19 |  | 0.1357 |  |  | 0.6785 |  |  |  | 25 | 0.1709 | 75 | 0.2021 | 1080.254 |  | Southwire | HD Copper : 350 : 350 - 19 : 19
HD Copper | 350 - 12 | 350 | 12 |  | 0.1708 |  |  | 0.70967 |  |  |  | 25 | 0.1709 | 75 | 0.2021 | 1080.8603 |  | Southwire | HD Copper : 350 : 350 - 12 : 12
HD Copper | 400 - 37 | 400 | 37 |  | 0.104 |  |  | 0.728 |  |  |  | 25 | 0.1501 | 75 | 0.1773 | 1235.6088 |  | Southwire | HD Copper : 400 : 400 - 37 : 37
HD Copper | 400 - 19 | 400 | 19 |  | 0.1451 |  |  | 0.7255 |  |  |  | 25 | 0.1501 | 75 | 0.1773 | 1235.0969 |  | Southwire | HD Copper : 400 : 400 - 19 : 19
HD Copper | 450 - 37 | 450 | 37 |  | 0.1103 |  |  | 0.7721 |  |  |  | 25 | 0.1339 | 75 | 0.158 | 1389.8417 |  | Southwire | HD Copper : 450 : 450 - 37 : 37
HD Copper | 450 - 19 | 450 | 19 |  | 0.1539 |  |  | 0.7695 |  |  |  | 25 | 0.1339 | 75 | 0.158 | 1389.4516 |  | Southwire | HD Copper : 450 : 450 - 19 : 19
HD Copper |  | 500 | 19 |  | 0.1622 |  |  | 0.811 |  |  |  | 20 | 0.11825 | 100 | 0.14953 | 1544 |  | Old Pjm | HD Copper : 500 : : 19
HD Copper | 500 - 37 | 500 | 37 |  | 0.1162 |  |  | 0.8134 |  |  |  | 25 | 0.121 | 75 | 0.1426 | 1542.505 |  | Southwire | HD Copper : 500 : 500 - 37 : 37
HD Copper | 500 - 19 | 500 | 19 |  | 0.1622 |  |  | 0.811 |  |  |  | 25 | 0.121 | 75 | 0.1426 | 1543.3623 |  | Southwire | HD Copper : 500 : 500 - 19 : 19
HD Copper | 600 - 61 | 600 | 61 |  | 0.0992 |  |  | 0.8928 |  |  |  | 25 | 0.1018 | 75 | 0.1196 | 1853.3855 |  | Southwire | HD Copper : 600 : 600 - 61 : 61
HD Copper | 600 - 37 | 600 | 37 |  | 0.1273 |  |  | 0.8911 |  |  |  | 25 | 0.1018 | 75 | 0.1196 | 1851.2758 |  | Southwire | HD Copper : 600 : 600 - 37 : 37
HD Copper | 700 - 61 | 700 | 61 |  | 0.1071 |  |  | 0.9639 |  |  |  | 25 | 0.0881 | 75 | 0.1033 | 2160.3363 |  | Southwire | HD Copper : 700 : 700 - 61 : 61
HD Copper | 700 - 37 | 700 | 37 |  | 0.1375 |  |  | 0.9625 |  |  |  | 25 | 0.0881 | 75 | 0.1033 | 2159.8307 |  | Southwire | HD Copper : 700 : 700 - 37 : 37
HD Copper | 750 - 61 | 750 | 61 |  | 0.1109 |  |  | 0.9981 |  |  |  | 25 | 0.0827 | 75 | 0.0969 | 2316.3571 |  | Southwire | HD Copper : 750 : 750 - 61 : 61
HD Copper | 750 - 37 | 750 | 37 |  | 0.1424 |  |  | 0.9968 |  |  |  | 25 | 0.0827 | 75 | 0.0969 | 2316.5106 |  | Southwire | HD Copper : 750 : 750 - 37 : 37
HD Copper | 800 - 61 | 800 | 61 |  | 0.1145 |  |  | 1.0305 |  |  |  | 25 | 0.0781 | 75 | 0.0912 | 2469.1837 |  | Southwire | HD Copper : 800 : 800 - 61 : 61
HD Copper | 800 - 37 | 800 | 37 |  | 0.147 |  |  | 1.029 |  |  |  | 25 | 0.0781 | 75 | 0.0912 | 2468.5901 |  | Southwire | HD Copper : 800 : 800 - 37 : 37
HD Copper | 900 - 61 | 900 | 61 |  | 0.1215 |  |  | 1.0935 |  |  |  | 25 | 0.0703 | 75 | 0.0819 | 2780.3213 |  | Southwire | HD Copper : 900 : 900 - 61 : 61
HD Copper | 900 - 37 | 900 | 37 |  | 0.156 |  |  | 1.092 |  |  |  | 25 | 0.0703 | 75 | 0.0819 | 2780.1198 |  | Southwire | HD Copper : 900 : 900 - 37 : 37
HD Copper | 1000 - 61 | 1000 | 61 |  | 0.128 |  |  | 1.152 |  |  |  | 25 | 0.0642 | 75 | 0.0745 | 3085.7616 |  | Southwire | HD Copper : 1000 : 1000 - 61 : 61
HD Copper | 1000 - 37 | 1000 | 37 |  | 0.1644 |  |  | 1.1508 |  |  |  | 25 | 0.0642 | 75 | 0.0745 | 3087.578 |  | Southwire | HD Copper : 1000 : 1000 - 37 : 37
HD Copper | 1250 - 61 | 1250 | 61 |  | 0.1431 |  |  | 1.288 |  |  |  | 25 | 0.0533 | 75 | 0.0613 | 3859 |  | Southwire | HD Copper : 1250 : 1250 - 61 : 61
HD Copper | 1500 - 61 | 1500 | 61 |  | 0.1568 |  |  | 1.411 |  |  |  | 25 | 0.0463 | 75 | 0.0528 | 4631 |  | Southwire | HD Copper : 1500 : 1500 - 61 : 61
HD Copper | 1750 - 91 | 1750 | 91 |  | 0.1387 |  |  | 1.526 |  |  |  | 25 | 0.0415 | 75 | 0.0469 | 5403 |  | Southwire | HD Copper : 1750 : 1750 - 91 : 91
HD Copper | 2000 - 91 | 2000 | 91 |  | 0.1482 |  |  | 1.63 |  |  |  | 25 | 0.0379 | 75 | 0.0426 | 6175 |  | Southwire | HD Copper : 2000 : 2000 - 91 : 91
VR2AAC | Rose/VR2 (2 x #4) | 83.5 | 7 |  | 0.0772 |  |  | 0.348 |  |  |  | 25 | 1.1153 | 75 | 1.3361 | 78.3 |  | Southwire | VR2AAC : 83.5 : Rose/VR2 (2 x #4) : 7
VR2AAC | Lily/VR2 (2 x #3) | 105.2 | 7 |  | 0.0867 |  |  | 0.39 |  |  |  | 25 | 0.8854 | 75 | 1.0606 | 98.7 |  | Southwire | VR2AAC : 105.2 : Lily/VR2 (2 x #3) : 7
VR2AAC | Iris/VR2 (2 x #2) | 132.7 | 7 |  | 0.0974 |  |  | 0.438 |  |  |  | 25 | 0.7021 | 75 | 0.8409 | 124.5 |  | Southwire | VR2AAC : 132.7 : Iris/VR2 (2 x #2) : 7
VR2AAC | Pansy/VR2 (2 x #1) | 167.4 | 7 |  | 0.1093 |  |  | 0.492 |  |  |  | 25 | 0.5568 | 75 | 0.6668 | 156.9 |  | Southwire | VR2AAC : 167.4 : Pansy/VR2 (2 x #1) : 7
VR2AAC | Poppy/VR2 (2 x #1/0) | 211.2 | 7 |  | 0.1228 |  |  | 0.552 |  |  |  | 25 | 0.4416 | 75 | 0.5287 | 198.1 |  | Southwire | VR2AAC : 211.2 : Poppy/VR2 (2 x #1/0) : 7
VR2AAC | Aster/VR2 (2 x #2/0) | 266.2 | 7 |  | 0.1379 |  |  | 0.621 |  |  |  | 25 | 0.3507 | 75 | 0.4198 | 249.8 |  | Southwire | VR2AAC : 266.2 : Aster/VR2 (2 x #2/0) : 7
VR2AAC | Phlox/VR2 (2 x #3/0) | 335.6 | 7 |  | 0.1548 |  |  | 0.696 |  |  |  | 25 | 0.2786 | 75 | 0.3333 | 314.8 |  | Southwire | VR2AAC : 335.6 : Phlox/VR2 (2 x #3/0) : 7
VR2AAC | Oxlip/VR2 (2 x #4/0) | 423.2 | 7 |  | 0.1739 |  |  | 0.783 |  |  |  | 25 | 0.2214 | 75 | 0.2648 | 397.2 |  | Southwire | VR2AAC : 423.2 : Oxlip/VR2 (2 x #4/0) : 7
VR2AAC | Daisy/VR2 (2 x 266.8) | 533.6 | 7 |  | 0.1953 |  |  | 0.879 |  |  |  | 25 | 0.1763 | 75 | 0.2105 | 501 |  | Southwire | VR2AAC : 533.6 : Daisy/VR2 (2 x 266.8) : 7
VR2AAC | Laurel/VR2 (2 x 266.8-19) | 533.6 | 19 |  | 0.1185 |  |  | 0.8895 |  |  |  | 25 | 0.1763 | 75 | 0.2105 | 500.1 |  | Southwire | VR2AAC : 533.6 : Laurel/VR2 (2 x 266.8-19) : 19
VR2AAC | Tulip/VR2 (2 x 336.4) | 672.8 | 19 |  | 0.1331 |  |  | 0.999 |  |  |  | 25 | 0.1406 | 75 | 0.1677 | 631.6 |  | Southwire | VR2AAC : 672.8 : Tulip/VR2 (2 x 336.4) : 19
VR2AAC | Daffofil/VR2 (2 x 350-19) | 700 | 19 |  | 0.1357 |  |  | 1.0185 |  |  |  | 25 | 0.1353 | 75 | 0.1613 | 655.9 |  | Southwire | VR2AAC : 700 : Daffofil/VR2 (2 x 350-19) : 19
VR2AAC | Canna/VR2 (2 x 397.5) | 795 | 19 |  | 0.1447 |  |  | 1.086 |  |  |  | 25 | 0.1198 | 75 | 0.1425 | 746.5 |  | Southwire | VR2AAC : 795 : Canna/VR2 (2 x 397.5) : 19
VR2AAC | Syringa/VR2 (2 x 477-37) | 954 | 37 |  | 0.1135 |  |  | 1.1925 |  |  |  | 25 | 0.1007 | 75 | 0.1196 | 893.5 |  | Southwire | VR2AAC : 954 : Syringa/VR2 (2 x 477-37) : 37
VR2AAC | Cosmos/VR2 (2 x 477.0) | 954 | 19 |  | 0.1584 |  |  | 1.1895 |  |  |  | 25 | 0.1007 | 75 | 0.1196 | 894.6 |  | Southwire | VR2AAC : 954 : Cosmos/VR2 (2 x 477.0) : 19
VR2AAC | Hyacinth/VR2 (2 x 500-37) | 1000 | 37 |  | 0.1622 |  |  | 1.2195 |  |  |  | 25 | 0.0964 | 75 | 0.1143 | 936.5 |  | Southwire | VR2AAC : 1000 : Hyacinth/VR2 (2 x 500-37) : 37
VR2AAC | Zinnia/VR2 (2 x 500-19) | 1000 | 19 |  | 0.1622 |  |  | 1.2165 |  |  |  | 25 | 0.0964 | 75 | 0.1143 | 937 |  | Southwire | VR2AAC : 1000 : Zinnia/VR2 (2 x 500-19) : 19
VR2AAC | Mistletoe/VR2 (2 x 556.5-37) | 1113 | 37 |  | 0.1226 |  |  | 1.287 |  |  |  | 25 | 0.0873 | 75 | 0.1033 | 1043 |  | Southwire | VR2AAC : 1113 : Mistletoe/VR2 (2 x 556.5-37) : 37
VR2AAC | Dahlia/VR2 (2 x 556.5) | 1113 | 19 |  | 0.1711 |  |  | 1.284 |  |  |  | 25 | 0.0873 | 75 | 0.1033 | 1044 |  | Southwire | VR2AAC : 1113 : Dahlia/VR2 (2 x 556.5) : 19
VR2AAC | Meadowsweet/VR2 (2 x 600-37) | 1200 | 37 |  | 0.1273 |  |  | 1.3365 |  |  |  | 25 | 0.0815 | 75 | 0.0962 | 1124 |  | Southwire | VR2AAC : 1200 : Meadowsweet/VR2 (2 x 600-37) : 37
VR2AAC | Orchid/VR2 (2 x 636-37) | 1272 | 37 |  | 0.1311 |  |  | 1.377 |  |  |  | 25 | 0.0773 | 75 | 0.0912 | 1192 |  | Southwire | VR2AAC : 1272 : Orchid/VR2 (2 x 636-37) : 37
VR2AAC | Nasturtium/VR2 (2 x 715.5-61) | 1431 | 61 |  | 0.1083 |  |  | 1.4625 |  |  |  | 25 | 0.0696 | 75 | 0.0818 | 1341 |  | Southwire | VR2AAC : 1431 : Nasturtium/VR2 (2 x 715.5-61) : 61
VR2AAC | Violet/VR2 (2 x 715.5-37) | 1431 | 37 |  | 0.1391 |  |  | 1.461 |  |  |  | 25 | 0.0696 | 75 | 0.0818 | 1342 |  | Southwire | VR2AAC : 1431 : Violet/VR2 (2 x 715.5-37) : 37
VR2AAC | Petunia/VR2 (2 x 750-37) | 1500 | 37 |  | 0.1424 |  |  | 1.4955 |  |  |  | 25 | 0.0668 | 75 | 0.0784 | 1407 |  | Southwire | VR2AAC : 1500 : Petunia/VR2 (2 x 750-37) : 37
VR2AAC | Lilac/VR2 (2 x 795-61) | 1590 | 61 |  | 0.1142 |  |  | 1.542 |  |  |  | 25 | 0.0636 | 75 | 0.0744 | 1491 |  | Southwire | VR2AAC : 1590 : Lilac/VR2 (2 x 795-61) : 61
VR2AAC | Arbutus/VR2 (2 x 795-37) | 1590 | 37 |  | 0.1466 |  |  | 1.539 |  |  |  | 25 | 0.0636 | 75 | 0.0744 | 1491 |  | Southwire | VR2AAC : 1590 : Arbutus/VR2 (2 x 795-37) : 37
VR2AAC | Cockscomb/VR2 (2 x 900-37) | 1800 | 37 |  | 0.156 |  |  | 1.638 |  |  |  | 25 | 0.0573 | 75 | 0.0667 | 1688 |  | Southwire | VR2AAC : 1800 : Cockscomb/VR2 (2 x 900-37) : 37
VR2AAC | Goldenrod/VR2 (2 x 954-61) | 1908 | 61 |  | 0.1251 |  |  | 1.689 |  |  |  | 25 | 0.0546 | 75 | 0.0635 | 1790 |  | Southwire | VR2AAC : 1908 : Goldenrod/VR2 (2 x 954-61) : 61
VR2AAC | Magnolia/VR2 (2 x 954-37) | 1908 | 37 |  | 0.1606 |  |  | 1.686 |  |  |  | 25 | 0.0546 | 75 | 0.0635 | 1789 |  | Southwire | VR2AAC : 1908 : Magnolia/VR2 (2 x 954-37) : 37
VR2AAC | Camellia/VR2 (2 x 1000-61) | 2000 | 61 |  | 0.128 |  |  | 1.728 |  |  |  | 25 | 0.0526 | 75 | 0.061 | 1874 |  | Southwire | VR2AAC : 2000 : Camellia/VR2 (2 x 1000-61) : 61
VR2AAC | Larkspur/VR2 (2 x 1033.5-61) | 2067 | 61 |  | 0.1302 |  |  | 1.758 |  |  |  | 25 | 0.0517 | 75 | 0.0598 | 1939 |  | Southwire | VR2AAC : 2067 : Larkspur/VR2 (2 x 1033.5-61) : 61
VR2AAC | Bluebell/VR2 (2 x 1033.5-37) | 2067 | 37 |  | 0.1671 |  |  | 1.755 |  |  |  | 25 | 0.0517 | 75 | 0.0598 | 1937 |  | Southwire | VR2AAC : 2067 : Bluebell/VR2 (2 x 1033.5-37) : 37
VR2AAC | Marigold/VR2 (2 x 1113-61) | 2226 | 61 |  | 0.1351 |  |  | 1.824 |  |  |  | 25 | 0.0488 | 75 | 0.0563 | 2087 |  | Southwire | VR2AAC : 2226 : Marigold/VR2 (2 x 1113-61) : 61
VR2ACSR | Swan/VR2 | 83.5 | 6 | 1 | 0.0834 | 0.0834 | 0.0834 | 0.375 | 3.35 |  |  | 25 | 1.0976 | 75 | 1.3884 | 78.3 | 36.8 | Southwire | VR2ACSR : 83.5 : Swan/VR2 : 6/1
VR2ACSR | Swallow/VR2 | 105.2 | 6 | 1 | 0.0937 | 0.0937 | 0.0937 | 0.4215 | 5.98 |  |  | 25 | 0.8713 | 75 | 1.0978 | 98.4 | 46.6 | Southwire | VR2ACSR : 105.2 : Swallow/VR2 : 6/1
VR2ACSR | Sparrow/VR2 | 132.7 | 6 | 1 | 0.1052 | 0.1052 | 0.1052 | 0.474 | 4.23 |  |  | 25 | 0.6909 | 75 | 0.9007 | 124 | 58.7 | Southwire | VR2ACSR : 132.7 : Sparrow/VR2 : 6/1
VR2ACSR | Robin/VR2 | 167.4 | 6 | 1 | 0.1181 | 0.1182 | 0.1182 | 0.5325 | 4.75 |  |  | 25 | 0.5478 | 75 | 0.7292 | 156.3 | 73.9 | Southwire | VR2ACSR : 167.4 : Robin/VR2 : 6/1
VR2ACSR | Raven/VR2 | 211.2 | 6 | 1 | 0.1327 | 0.1327 | 0.1327 | 0.597 | 5.33 |  |  | 25 | 0.4344 | 75 | 0.5937 | 197.3 | 93.4 | Southwire | VR2ACSR : 211.2 : Raven/VR2 : 6/1
VR2ACSR | Ortolan/VR2 | 2067 | 45 | 7 | 0.1515 | 0.101 | 0.303 | 1.818 |  |  |  | 25 | 0.0503 | 75 | 0.5871 | 1947 | 380 | Southwire | VR2ACSR : 2067 : Ortolan/VR2 : 45/7
VR2ACSR | Quail/VR2 | 266.2 | 6 | 1 | 0.1489 | 0.1489 | 0.1489 | 0.6705 | 5.99 |  |  | 25 | 0.345 | 75 | 0.4879 | 248.4 | 117.5 | Southwire | VR2ACSR : 266.2 : Quail/VR2 : 6/1
VR2ACSR | Pigeon/VR2 | 335.6 | 6 | 1 | 0.1672 | 0.1672 | 0.1672 | 0.753 | 6.72 |  |  | 25 | 0.274 | 75 | 0.4036 | 313.2 | 148.2 | Southwire | VR2ACSR : 335.6 : Pigeon/VR2 : 6/1
VR2ACSR | Penguin/VR2 | 423.2 | 6 | 1 | 0.1878 | 0.1878 | 0.1878 | 0.8445 | 7.55 |  |  | 25 | 0.2177 | 75 | 0.3349 | 395.1 | 187 | Southwire | VR2ACSR : 423.2 : Penguin/VR2 : 6/1
VR2ACSR | Jaeger/VR2 | 456.4 | 18 | 1 | 0.1126 | 0.1126 | 0.1126 | 0.8445 | 10.14 |  |  | 25 | 0.2046 | 75 | 0.2446 | 428.2 | 67.2 | Southwire | VR2ACSR : 456.4 : Jaeger/VR2 : 18/1
VR2ACSR | Partridge/VR2 | 533.6 | 26 | 7 | 0.1013 | 0.0788 | 0.2364 | 0.963 |  |  |  | 25 | 0.1748 | 75 | 0.2089 | 503.1 | 231.4 | Southwire | VR2ACSR : 533.6 : Partridge/VR2 : 26/7
VR2ACSR | Waxwing/VR2 | 672.8 | 6 | 7 | 0.1217 | 0.1217 | 0.1217 | 0.9135 |  |  |  | 25 | 0.1725 | 75 | 0.2059 | 500.3 | 78.5 | Southwire | VR2ACSR : 672.8 : Waxwing/VR2 : 6/7
VR2ACSR | Merlin/VR2 | 672.8 | 18 | 1 | 0.1367 | 0.1367 | 0.1367 | 1.026 |  |  |  | 25 | 0.1399 | 75 | 0.1669 | 631.2 | 99.1 | Southwire | VR2ACSR : 672.8 : Merlin/VR2 : 18/1
VR2ACSR | Linnet/VR2 | 672.8 | 26 | 7 | 0.1137 | 0.0884 | 0.2652 | 1.08 |  |  |  | 25 | 0.1393 | 75 | 0.1662 | 633.8 | 291.2 | Southwire | VR2ACSR : 672.8 : Linnet/VR2 : 26/7
VR2ACSR | Oriole/VR2 | 672.8 | 30 | 7 | 0.1059 | 0.1059 | 0.3177 | 1.1115 |  |  |  | 25 | 0.1368 | 75 | 0.1631 | 635 | 418 | Southwire | VR2ACSR : 672.8 : Oriole/VR2 : 30/7
VR2ACSR | Ptarmigan/VR2 | 795 | 20 | 7 | 0.141 | 0.0627 | 0.1881 | 1.128 |  |  |  | 25 | 0.1194 | 75 | 0.1422 | 749 | 146.4 | Southwire | VR2ACSR : 795 : Ptarmigan/VR2 : 20/7
VR2ACSR | Chickadee/VR2 | 795 | 18 | 1 | 0.1486 | 0.1486 | 0.1486 | 1.1145 |  |  |  | 25 | 0.1191 | 75 | 0.1418 | 745.9 | 117.1 | Southwire | VR2ACSR : 795 : Chickadee/VR2 : 18/1
VR2ACSR | Ibis/VR2 | 795 | 26 | 7 | 0.1236 | 0.0961 | 0.2883 | 1.1745 |  |  |  | 25 | 0.1184 | 75 | 0.1411 | 749 | 334.1 | Southwire | VR2ACSR : 795 : Ibis/VR2 : 26/7
VR2ACSR | Brant/VR2 | 795 | 24 | 7 | 0.1287 | 0.0858 | 0.2547 | 1.158 |  |  |  | 25 | 0.1178 | 75 | 0.1403 | 749 | 274 | Southwire | VR2ACSR : 795 : Brant/VR2 : 24/7
VR2ACSR | Lark/VR2 | 795 | 30 | 7 | 0.1151 | 0.1151 | 0.3453 | 1.209 |  |  |  | 25 | 0.1163 | 75 | 0.1385 | 751 | 493 | Southwire | VR2ACSR : 795 : Lark/VR2 : 30/7
VR2ACSR | Tailorbird/VR2 | 954 | 20 | 7 | 0.1544 | 0.0686 | 0.2058 | 1.236 |  |  |  | 25 | 0.1003 | 75 | 0.1192 | 899.1 | 175.3 | Southwire | VR2ACSR : 954 : Tailorbird/VR2 : 20/7
VR2ACSR | Pelican/VR2 | 954 | 18 | 1 | 0.1628 | 0.1628 | 0.1628 | 1.221 |  |  |  | 25 | 0.1001 | 75 | 0.1189 | 895.2 | 140.5 | Southwire | VR2ACSR : 954 : Pelican/VR2 : 18/1
VR2ACSR | Flicker/VR2 | 954 | 24 | 7 | 0.141 | 0.094 | 0.282 | 1.269 |  |  |  | 25 | 0.0997 | 75 | 0.1185 | 898.8 | 329.2 | Southwire | VR2ACSR : 954 : Flicker/VR2 : 24/7
VR2ACSR | Hawk/VR2 | 954 | 26 | 7 | 0.1354 | 0.1053 | 0.3159 | 1.287 |  |  |  | 25 | 0.0994 | 75 | 0.1182 | 898.8 | 413.1 | Southwire | VR2ACSR : 954 : Hawk/VR2 : 26/7
VR2ACSR | Hen/VR2 | 954 | 30 | 7 | 0.1261 | 0.1261 | 0.3783 | 1.3245 |  |  |  | 25 | 0.099 | 75 | 0.1178 | 901.7 | 592.5 | Southwire | VR2ACSR : 954 : Hen/VR2 : 30/7
VR2ACSR | Nightingale/VR2 | 1033.5 | 18 | 1 | 0.1694 | 0.1694 | 0.1694 | 1.2705 | 15.25 |  |  | 25 | 0.093 | 75 | 0.1104 | 973.9 | 189.9 | Southwire | VR2ACSR : 1033.5 : Nightingale/VR2 : 18/1
VR2ACSR | Creeper/VR2 | 1033.5 | 20 | 7 | 0.1607 | 0.0714 | 0.2142 | 1.2855 |  |  |  | 25 | 0.0928 | 75 | 0.1101 | 969.3 | 152.1 | Southwire | VR2ACSR : 1033.5 : Creeper/VR2 : 20/7
VR2ACSR | Tody/VR2 | 1113 | 20 | 7 | 0.1668 | 0.0741 | 0.2223 | 1.335 |  |  |  | 25 | 0.0868 | 75 | 0.1029 | 1048 | 204.6 | Southwire | VR2ACSR : 1113 : Tody/VR2 : 20/7
VR2ACSR | Osprey/VR2 | 1113 | 18 | 1 | 0.1758 | 0.1758 | 0.1758 | 1.3185 | 9.669 |  |  | 25 | 0.0866 | 75 | 0.1026 | 1044 | 163.8 | Southwire | VR2ACSR : 1113 : Osprey/VR2 : 18/1
VR2ACSR | Parakeet/VR2 | 1113 | 24 | 7 | 0.1523 | 0.1015 | 0.3045 | 1.371 |  |  |  | 25 | 0.0862 | 75 | 0.1022 | 1049 | 383.6 | Southwire | VR2ACSR : 1113 : Parakeet/VR2 : 24/7
VR2ACSR | Dove/VR2 | 1113 | 26 | 7 | 0.1463 | 0.1138 | 0.3414 | 1.3905 |  |  |  | 25 | 0.0851 | 75 | 0.1009 | 1048 | 482 | Southwire | VR2ACSR : 1113 : Dove/VR2 : 26/7
VR2ACSR | Eagle/VR2 | 1113 | 30 | 7 | 0.1362 | 0.1362 | 0.4086 | 1.4295 |  |  |  | 25 | 0.0843 | 75 | 0.1 | 1051 | 690 | Southwire | VR2ACSR : 1113 : Eagle/VR2 : 30/7
VR2ACSR | Peacock/VR2 | 1210 | 24 | 7 | 0.1588 | 0.1059 | 0.3177 | 1.4295 |  |  |  | 25 | 0.0792 | 75 | 0.0937 | 1140 | 417 | Southwire | VR2ACSR : 1210 : Peacock/VR2 : 24/7
VR2ACSR | Squab/VR2 | 1210 | 26 | 7 | 0.1525 | 0.1186 | 0.3558 | 1.449 |  |  |  | 25 | 0.0787 | 75 | 0.0932 | 1140 | 524 | Southwire | VR2ACSR : 1210 : Squab/VR2 : 26/7
VR2ACSR | Teal/VR2 | 1210 | 30 | 19 | 0.0852 | 0.0852 | 0.426 | 1.491 |  |  |  | 25 | 0.078 | 75 | 0.0924 | 1142 | 735 | Southwire | VR2ACSR : 1210 : Teal/VR2 : 30/19
VR2ACSR | Wood Duck/VR2 | 1210 | 30 | 7 | 0.142 | 0.142 | 0.426 | 1.491 |  |  |  | 25 | 0.078 | 75 | 0.0923 | 1142 | 751 | Southwire | VR2ACSR : 1210 : Wood Duck/VR2 : 30/7
VR2ACSR | Swift/VR2 | 1272 | 36 | 1 | 0.1329 | 0.1329 | 0.1329 | 1.395 |  |  |  | 25 | 0.0768 | 75 | 0.0906 | 1192 | 94 | Southwire | VR2ACSR : 1272 : Swift/VR2 : 36/1
VR2ACSR | Rook/VR2 | 1272 | 24 | 7 | 0.1628 | 0.1085 | 0.3255 | 1.4655 |  |  |  | 25 | 0.0756 | 75 | 0.0894 | 1198 | 439 | Southwire | VR2ACSR : 1272 : Rook/VR2 : 24/7
VR2ACSR | Grosbeak/VR2 | 1272 | 26 | 7 | 0.1564 | 0.1216 | 0.3648 | 1.485 |  |  |  | 25 | 0.0752 | 75 | 0.0889 | 1198 | 551 | Southwire | VR2ACSR : 1272 : Grosbeak/VR2 : 26/7
VR2ACSR | Scoter/VR2 | 1272 | 30 | 7 | 0.1456 | 0.1456 | 0.4368 | 1.5285 |  |  |  | 25 | 0.0745 | 75 | 0.0881 | 1201 | 789 | Southwire | VR2ACSR : 1272 : Scoter/VR2 : 30/7
VR2ACSR | Egret/VR2 | 1272 | 30 | 19 | 0.1456 | 0.0874 | 0.437 | 1.5285 |  |  |  | 25 | 0.0745 | 75 | 0.0881 | 1201 | 773 | Southwire | VR2ACSR : 1272 : Egret/VR2 : 30/19
VR2ACSR | Flamingo/VR2 | 1333.2 | 24 | 7 | 0.1667 | 0.111 | 0.333 | 1.5 |  |  |  | 25 | 0.0724 | 75 | 0.0855 | 1256 | 495 | Southwire | VR2ACSR : 1333.2 : Flamingo/VR2 : 24/7
VR2ACSR | Gannet/VR2 | 1333.2 | 26 | 7 | 0.1601 | 0.1245 | 0.3735 | 1.521 |  |  |  | 25 | 0.0721 | 75 | 0.085 | 1256 | 577 | Southwire | VR2ACSR : 1333.2 : Gannet/VR2 : 26/7
VR2ACSR | Stilt/VR2 | 1431 | 24 | 7 | 0.1727 | 0.1151 | 0.3453 | 1.554 |  |  |  | 25 | 0.068 | 75 | 0.0801 | 1348 | 493 | Southwire | VR2ACSR : 1431 : Stilt/VR2 : 24/7
VR2ACSR | Starling/VR2 | 1431 | 26 | 7 | 0.1659 | 0.129 | 0.387 | 1.5765 |  |  |  | 25 | 0.0675 | 75 | 0.0796 | 1348 | 620 | Southwire | VR2ACSR : 1431 : Starling/VR2 : 26/7
VR2ACSR | Redwing/VR2 | 1431 | 30 | 19 | 0.1544 | 0.0926 | 0.463 | 1.6215 |  |  |  | 25 | 0.0669 | 75 | 0.0789 | 1351 | 869 | Southwire | VR2ACSR : 1431 : Redwing/VR2 : 30/19
VR2ACSR | Condor/VR2 | 1590 | 54 | 7 | 0.1213 | 0.1213 | 0.3639 | 1.63 |  |  |  | 25 | 0.0619 | 75 | 0.0745 | 1498 | 548 | Southwire | VR2ACSR : 1590 : Condor/VR2 : 54/7
VR2ACSR | Tern/VR2 | 1590 | 45 | 7 | 0.1329 | 0.0886 | 0.2658 | 1.5945 |  |  |  | 25 | 0.0627 | 75 | 0.074 | 1498 | 292 | Southwire | VR2ACSR : 1590 : Tern/VR2 : 45/7
VR2ACSR | Coot/VR2 | 1590 | 36 | 1 | 0.1486 | 0.1486 | 0.1486 | 1.56 |  |  |  | 25 | 0.0631 | 75 | 0.0739 | 1490 | 117 | Southwire | VR2ACSR : 1590 : Coot/VR2 : 36/1
VR2ACSR | Cuckoo/VR2 | 1590 | 24 | 7 | 0.182 | 0.1213 | 0.3639 | 1.63 |  |  |  | 25 | 0.0619 | 75 | 0.0727 | 1000 | 300 | Southwire | VR2ACSR : 1590 : Cuckoo/VR2 : 24/7
VR2ACSR | Drake/VR2 | 1590 | 26 | 7 | 0.1749 | 0.136 | 0.408 | 1.662 |  |  |  | 25 | 0.0615 | 75 | 0.0723 | 1498 | 688 | Southwire | VR2ACSR : 1590 : Drake/VR2 : 26/7
VR2ACSR | Mallard/VR2 | 1590 | 30 | 19 | 0.1628 | 0.0977 | 0.4885 | 1.71 |  |  |  | 25 | 0.0609 | 75 | 0.0716 | 1501 | 966 | Southwire | VR2ACSR : 1590 : Mallard/VR2 : 30/19
VR2ACSR | Canary/VR2 | 1800 | 54 | 7 | 0.1291 | 0.1291 | 0.3873 | 1.743 |  |  |  | 25 | 0.0556 | 75 | 0.0666 | 1695 | 621 | Southwire | VR2ACSR : 1800 : Canary/VR2 : 54/7
VR2ACSR | Ruddy/VR2 | 1800 | 45 | 7 | 0.1414 | 0.0943 | 0.2829 | 1.6965 |  |  |  | 25 | 0.0564 | 75 | 0.0662 | 1695 | 331 | Southwire | VR2ACSR : 1800 : Ruddy/VR2 : 45/7
VR2ACSR | Cardinal/VR2 | 1908 | 54 | 7 | 0.1329 | 0.1329 | 0.3987 | 1.794 |  |  |  | 25 | 0.053 | 75 | 0.0633 | 1797 | 657 | Southwire | VR2ACSR : 1908 : Cardinal/VR2 : 54/7
VR2ACSR | Rail/VR2 | 1908 | 45 | 7 | 0.1456 | 0.0971 | 0.2913 | 1.7475 |  |  |  | 25 | 0.0537 | 75 | 0.0629 | 1797 | 351 | Southwire | VR2ACSR : 1908 : Rail/VR2 : 45/7
VR2ACSR | Curlew/VR2 | 2067 | 54 | 7 | 0.1383 | 0.1383 | 0.4149 | 1.8675 |  |  |  | 25 | 0.0496 | 75 | 0.059 | 1947 | 712 | Southwire | VR2ACSR : 2067 : Curlew/VR2 : 54/7
VR2ACSR | Finch/VR2 | 2226 | 54 | 19 | 0.1436 | 0.0862 | 0.431 | 1.9395 |  |  |  | 25 | 0.0469 | 75 | 0.0556 | 2107 | 751 | Southwire | VR2ACSR : 2226 : Finch/VR2 : 54/19
VR2ACSR | Bluejay/VR2 | 2226 | 45 | 7 | 0.1573 | 0.1049 | 0.3147 | 1.8885 |  |  |  | 25 | 0.0475 | 75 | 0.0552 | 2097 | 409 | Southwire | VR2ACSR : 2226 : Bluejay/VR2 : 45/7
VR2ACSR | Bittern/VR2 | 2544 | 45 | 7 | 0.1681 | 0.1121 | 0.3363 | 2.206 |  |  |  | 25 | 0.0379 | 75 | 0.0452 |  |  | Southwire | VR2ACSR : 2544 : Bittern/VR2 : 45/7

## Day
Month | Days | TotalDays
1 | 31 | 0
2 | 28 | 31
3 | 31 | 59
4 | 30 | 90
5 | 31 | 120
6 | 30 | 151
7 | 31 | 181
8 | 31 | 212
9 | 30 | 243
10 | 31 | 273
11 | 30 | 304
12 | 31 | 334

## Dropdowns
Table 3
Atmosphere | a | b | c | d | e | f | g
Clear | -3.9241 | 5.9276 | -0.17856 | 0.003223 | -3.3549e-05 | 1.8053e-07 | -3.7868e-10
Industrial | 4.9408 | 1.3208 | 0.061444 | -0.0029411 | 5.0775e-05 | -4.0363e-07 | 1.2297e-09

## Rate
[13 empty] | Conductor | [7 empty] | Solar Heat Flux | [27 empty] | 6 | 13b - uf lb/ft-hr | 14b - ρf | 15b - kf | 2c - NRe | Limited to [0,90] |  | 4a | 5a - qc0 | 3a - qc1 | 3b - qc2 | qc - 4.4.3, Page 10, select the larger of the two calculated convection heat losses | qr 4.6.1.3 | qs
[14 empty] | Low Temp C | Low Resistance Ohm/ft | Hi Temp C | Hi Resistance Ohm/ft | Metal OD ft | 10 | 10 |  | Table 3 | [11 empty] | Hour angle relative to noon | Table H.5 | 16b | 16b | 16a | 16a - between 0-90. | 18 |  | Note: Sometimes Qs (18) calculates a negative value. Possibly due to a precision error with high degree order polynomials. | 17 |  | Azimuth of line | Azimuth of sun | 9 |  | tfilm | dynamic_viscosity | air_density | thermal_conductivity_of_air | reynolds_number | wind_angle_deg | wind_angle_rad | k_angle | natural_convection | low_wind_convection | high_wind_convection | convective_heat_loss | radiated_heat_loss | solar_heat_gain
DateTime | Ambient C | Wind Speed ft/s | Wind Angle deg | Latitude deg | Line Azimuth | Elevation ft | Atmosphere | Conductor | Emissivity | Absorptivity | MOT C | Current (A) | match_wire | t_low | r_low | t_high | r_high | D0 | per_1 | r_avg | match_atmosphere | a | b | c | d | e | f | g | month | day | day_of_year | hour_of_day | lat_rad | w_rad | mult | p | delta_rad | hC_rad | hC_deg | Q_s | Ksolar | Qse | X | cc | Zl_rad | Zc_rad | theta_rad | solar_heat_gain | tfilm | uf | pf | kf | Rne | phi_deg_limited | phi_rad | kangle | qc0 | qc1 | qc2 | qc | qr | qs
2023-06-10 11:00 | 30 | 0.6 | 90 | 30 | 90 | 0 | Clear | ACSR : 795 : Drake : 26/7 | 0.8 | 0.8 | 100 | 887.4892 | 322 | 25 | 2.2083e-05 | 75 | 2.6326e-05 | 0.092333 | 8.4848e-08 | 2.8447e-05 | 1 | -3.9241 | 5.9276 | -0.17856 | 0.003223 | -3.3549e-05 | 1.8053e-07 | -3.7868e-10 | 6 | 10 | 161 | 11 | 0.5236 | -0.2618 | 1 | 7.6603 | 0.40177 | 1.3071 | 74.8904 | 95.4374 | 1 | 95.4374 | -2.2505 | 180 | 1.5708 | 1.9889 | 1.3303 | 6.8467 | 65 | 0.048952 | 0.065153 | 0.0088637 | 265.4435 | 90 | 1.5708 | 1 | 15.7987 | 15.8851 | 13.3188 | 15.8851 | 13.3675 | 6.8467
2023-06-10 11:00 | 40 | 2 | 90 | 30 | 90 | 0 | Clear | ACSR : 795 : Drake : 26/7 | 0.8 | 0.8 | 100 | 1028.2845 | 322 | 25 | 2.2083e-05 | 75 | 2.6326e-05 | 0.092333 | 8.4848e-08 | 2.8447e-05 | 1 | -3.9241 | 5.9276 | -0.17856 | 0.003223 | -3.3549e-05 | 1.8053e-07 | -3.7868e-10 | 6 | 10 | 161 | 11 | 0.5236 | -0.2618 | 1 | 7.6603 | 0.40177 | 1.3071 | 74.8904 | 95.4374 | 1 | 95.4374 | -2.2505 | 180 | 1.5708 | 1.9889 | 1.3303 | 6.8467 | 70 | 0.04949 | 0.064202 | 0.0089767 | 862.4178 | 90 | 1.5708 | 1 | 12.9343 | 24.9882 | 23.4461 | 24.9882 | 11.9375 | 6.8467
2023-06-10 11:00 | 50 | 2 | 90 | 30 | 90 | 0 | Clear | ACSR : 795 : Drake : 26/7 | 0.8 | 0.8 | 100 | 924.8814 | 322 | 25 | 2.2083e-05 | 75 | 2.6326e-05 | 0.092333 | 8.4848e-08 | 2.8447e-05 | 1 | -3.9241 | 5.9276 | -0.17856 | 0.003223 | -3.3549e-05 | 1.8053e-07 | -3.7868e-10 | 6 | 10 | 161 | 11 | 0.5236 | -0.2618 | 1 | 7.6603 | 0.40177 | 1.3071 | 74.8904 | 95.4374 | 1 | 95.4374 | -2.2505 | 180 | 1.5708 | 1.9889 | 1.3303 | 6.8467 | 75 | 0.050024 | 0.063278 | 0.0090897 | 840.9353 | 90 | 1.5708 | 1 | 10.224 | 20.8168 | 19.4871 | 20.8168 | 10.3636 | 6.8467
2023-01-01 | 2.2 | 0 | 90 | 47.42 | 90 | 1843 | Clear | ACSR : 795 : Drake : 26/7 | 0.8 | 0.8 | 100 | 1191.1775 | 322 | 25 | 2.2083e-05 | 75 | 2.6326e-05 | 0.092333 | 8.4848e-08 | 2.8447e-05 | 1 | -3.9241 | 5.9276 | -0.17856 | 0.003223 | -3.3549e-05 | 1.8053e-07 | -3.7868e-10 | 1 | 1 | 1 | 0 | 0.82764 | -3.1416 | 1 | 4.906 | -0.40177 | -1.1449 | 0 | -3.9241 | 1.0611 | 0 | 2.7295e-16 | 0 | 1.5708 | 2.7295e-16 | 1.5708 | 0 | 51.1 | 0.047436 | 0.063555 | 0.0085491 | 0 | 90 | 1.5708 | 1 | 23.7018 | 0.84446 | 0 | 23.7018 | 16.6617 | 0
2023-06-10 11:00 | 40 | 2 | 90 | 47.42 | 90 | 1843 | Clear | ACSR : 795 : Drake : 26/7 | 0.8 | 0.8 | 90 | 902.9798 | 322 | 25 | 2.2083e-05 | 75 | 2.6326e-05 | 0.092333 | 8.4848e-08 | 2.7598e-05 | 1 | -3.9241 | 5.9276 | -0.17856 | 0.003223 | -3.3549e-05 | 1.8053e-07 | -3.7868e-10 | 6 | 10 | 161 | 11 | 0.82764 | -0.2618 | 1 | 7.6603 | 0.40177 | 1.0962 | 62.8058 | 93.6617 | 1.0611 | 99.3852 | -0.61077 | 180 | 1.5708 | 2.5933 | 1.3303 | 7.1299 | 65 | 0.048952 | 0.060937 | 0.0088637 | 827.5656 | 90 | 1.5708 | 1 | 10.0331 | 20.1344 | 18.8207 | 20.1344 | 9.4986 | 7.1299
Note on F4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: If line runs East to West, 90 deg.
Note on BB4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Since uf is in lb/ft-hr, we must use wind-speed Vw in ft/hr.